## 15mm
1/2" / 15mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 21.336 | 47.752 | 88.9 | 60.452 | 4 | 15.748
EN12560-1 | ASA150 | 21.336 | 47.752 | 88.9 | 60.452 | 4 | 15.748
Nominal Bore | ASA300 | 21.336 | 53.848 | 95.25 | 66.548 | 4 | 15.748
| ASA600 | 21.336 | 53.848 | 95.25 | 66.548 | 4 | 15.748
ANSI B16.21 & | ASA125 | 12.7 | 47.752 | 88.9 | 60.452 | 4 | 15.748
EN12560-1 | ASA150 | 12.7 | 47.752 | 88.9 | 60.452 | 4 | 15.748
True Bore | ASA300 | 12.7 | 53.848 | 95.25 | 66.548 | 4 | 15.748
| ASA600 | 12.7 | 53.848 | 95.25 | 66.548 | 4 | 15.748
BS3063 | BST A | 21.4312 | 52.3875 | 95.25 | 66.675 | 4 | 14.2875
Nominal Bore | BST D | 21.4312 | 52.3875 | 95.25 | 66.675 | 4 | 14.2875
| BST E | 21.4312 | 52.3875 | 95.25 | 66.675 | 4 | 14.2875
| BST F | 21.4312 | 63.5 | 114.3 | 82.55 | 4 | 19.05
| BST H | 21.4312 | 63.5 | 114.3 | 82.55 | 4 | 19.05
| BST J | 21.4312 | 63.5 | 115 | 82.6 | 4 | 19.1
| BST K | 21.4312 | 63.5 | 115 | 82.6 | 4 | 19.1
| BST R | 21.4312 | 63.5 | 115 | 82.6 | 4 | 19.1
BS3063 | BST A | 12.7 | 52.3875 | 95.25 | 66.675 | 4 | 14.2875
True Bore | BST D | 12.7 | 52.3875 | 95.25 | 66.675 | 4 | 14.2875
| BST E | 12.7 | 52.3875 | 95.25 | 66.675 | 4 | 14.2875
| BST F | 12.7 | 63.5 | 114.3 | 82.55 | 4 | 19.05
| BST H | 12.7 | 63.5 | 114.3 | 82.55 | 4 | 19.05
| BST J | 12.7 | 63.5 | 115 | 82.6 | 4 | 19.1
| BST K | 12.7 | 63.5 | 115 | 82.6 | 4 | 19.1
| BST R | 12.7 | 63.5 | 115 | 82.6 | 4 | 19.1
BS EN 1514-1 | PN2.5 | 22 | 43 | 80 | 55 | 4 | 11
& DIN2690 | PN6 | 22 | 43 | 80 | 55 | 4 | 11
| PN10 | 22 | 50 | 95 | 65 | 4 | 14
| PN16 | 22 | 50 | 95 | 65 | 4 | 14
| PN25 | 22 | 50 | 95 | 65 | 4 | 14
| PN40 | 22 | 50 | 95 | 65 | 4 | 14
AS4087 | Class 14/16 | 21.4 | 53 | 95 | 67 | 4 | 14
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 22 | 50 | 80 | 60 | 4 | 12
| 10K | 22 | 58 | 95 | 70 | 4 | 15
| 16K | 22 | 58 | 95 | 70 | 4 | 15
| 20K | 22 | 58 | 95 | 70 | 4 | 15
| 30K | 22 | 64 | 115 | 80 | 4 | 19
| 40K | 22 | 64 | 115 | 80 | 4 | 19
| 63K | 22 | 69 | 120 | 85 | 4 | 19
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | 22 | 44 | 80 | 55 | 4 | 11
| PN6 | 22 | 44 | 80 | 55 | 4 | 11
| PN10 | 22 | 51 | 95 | 65 | 4 | 14
| PN16 | 22 | 51 | 95 | 65 | 4 | 14
| PN20 | 22 | 46.5 | 90 | 60.5 | 4 | 16
| PN25 | 22 | 51 | 95 | 65 | 4 | 14
| PN40 | 22 | 51 | 95 | 65 | 4 | 14
| PN50 | 22 | 52.5 | - | - | - | -
| PN110 | 22 | 52.5 | - | - | - | -
| PN150 | 22 | 62.5 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 20mm
3/4" / 20mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 26.924 | 57.15 | 98.552 | 69.85 | 4 | 15.748
EN12560-1 | ASA150 | 26.924 | 57.15 | 98.552 | 69.85 | 4 | 15.748
Nominal Bore | ASA300 | 26.924 | 66.548 | 117.348 | 82.55 | 4 | 19.05
| ASA600 | 26.924 | 66.548 | 117.348 | 82.55 | 4 | 19.05
ANSI B16.21 & | ASA125 | 19.1 | 57.15 | 98.552 | 69.85 | 4 | 15.748
EN12560-1 | ASA150 | 19.1 | 57.15 | 98.552 | 69.85 | 4 | 15.748
True Bore | ASA300 | 19.1 | 66.548 | 117.348 | 82.55 | 4 | 19.05
| ASA600 | 19.1 | 66.548 | 117.348 | 82.55 | 4 | 19.05
BS3063 | BST A | 26.9875 | 58.7125 | 101.6 | 73 | 4 | 14.2875
Nominal Bore | BST D | 26.9875 | 58.7125 | 101.6 | 73 | 4 | 14.2875
| BST E | 26.9875 | 58.7125 | 101.6 | 73 | 4 | 14.2875
| BST F | 26.9875 | 58.7125 | 101.6 | 73 | 4 | 14.2875
| BST H | 26.9875 | 63.5 | 114.3 | 82.55 | 4 | 19.05
| BST J | 26.9875 | 63.5 | 114.3 | 82.55 | 4 | 19.05
| BST K | 26.9875 | 63.5 | 114.3 | 82.55 | 4 | 19.05
| BST R | 26.9875 | 63.5 | 114.3 | 82.55 | 4 | 19.05
BS3063 | BST A | 19.1 | 58.7125 | 101.6 | 73 | 4 | 14.2875
True Bore | BST D | 19.1 | 58.7125 | 101.6 | 73 | 4 | 14.2875
| BST E | 19.1 | 58.7125 | 101.6 | 73 | 4 | 14.2875
| BST F | 19.1 | 58.7125 | 101.6 | 73 | 4 | 14.2875
| BST H | 19.1 | 63.5 | 114.3 | 82.55 | 4 | 19.05
| BST J | 19.1 | 63.5 | 114.3 | 82.55 | 4 | 19.05
| BST K | 19.1 | 63.5 | 114.3 | 82.55 | 4 | 19.05
| BST R | 19.1 | 63.5 | 114.3 | 82.55 | 4 | 19.05
BS EN 1514-1 | PN2.5 | 28 | 53 | 90 | 65 | 4 | 11
& DIN2690 | PN6 | 28 | 53 | 90 | 65 | 4 | 11
| PN10 | 28 | 60 | 105 | 75 | 4 | 14
| PN16 | 28 | 60 | 105 | 75 | 4 | 14
| PN25 | 28 | 60 | 105 | 75 | 4 | 14
| PN40 | 28 | 60 | 105 | 75 | 4 | 14
AS4087 | Class 14/16 | 27 | 59 | 100 | 73 | 4 | 14
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 28 | 55 | 85 | 65 | 4 | 12
| 10K | 28 | 63 | 100 | 75 | 4 | 15
| 16K | 28 | 63 | 100 | 75 | 4 | 15
| 20K | 28 | 63 | 100 | 75 | 4 | 15
| 30K | 28 | 69 | 120 | 85 | 4 | 19
| 40K | 28 | 69 | 120 | 85 | 4 | 19
| 63K | 28 | 75 | 135 | 95 | 4 | 23
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | 29 | - | 90 | 65 | 4 | 11
| PN10 | 29 | - | 105 | 75 | 4 | 14
| PN16 | 29 | - | 105 | 75 | 4 | 14
| PN25 | 29 | - | 105 | 75 | 4 | 14
ISO7483 | PN2.5 | 27 | 54 | 90 | 65 | 4 | 11
| PN6 | 27 | 54 | 90 | 65 | 4 | 11
| PN10 | 27 | 61 | 105 | 75 | 4 | 14
| PN16 | 27 | 61 | 105 | 75 | 4 | 14
| PN20 | 27 | 56 | 100 | 70 | 4 | 16
| PN25 | 27 | 61 | 105 | 75 | 4 | 14
| PN40 | 27 | 61 | 105 | 75 | 4 | 14
| PN50 | 27 | 64.5 | - | - | - | -
| PN110 | 27 | 64.5 | - | - | - | -
| PN150 | 27 | 69 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 25mm
1" / 25mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 33.274 | 66.548 | 107.95 | 79.248 | 4 | 15.748
EN12560-1 | ASA150 | 33.274 | 66.548 | 107.95 | 79.248 | 4 | 15.748
Nominal Bore | ASA300 | 33.274 | 73.152 | 123.952 | 88.9 | 4 | 19.05
| ASA600 | 33.274 | 73.152 | 123.952 | 88.9 | 4 | 19.05
ANSI B16.21 & | ASA125 | 25.4 | 66.548 | 107.95 | 79.248 | 4 | 15.748
EN12560-1 | ASA150 | 25.4 | 66.548 | 107.95 | 79.248 | 4 | 15.748
True Bore | ASA300 | 25.4 | 73.152 | 123.952 | 88.9 | 4 | 19.05
| ASA600 | 25.4 | 73.152 | 123.952 | 88.9 | 4 | 19.05
BS3063 | BST A | 34.1313 | 68.2625 | 114.3 | 82.55 | 4 | 14.2875
Nominal Bore | BST D | 34.1313 | 68.2625 | 114.3 | 82.55 | 4 | 14.2875
| BST E | 34.1313 | 68.2625 | 114.3 | 82.55 | 4 | 14.2875
| BST F | 34.1313 | 68.2625 | 120.65 | 87.3125 | 4 | 19.05
| BST H | 34.1313 | 68.2625 | 120.65 | 87.3125 | 4 | 19.05
| BST J | 34.1313 | 68.2625 | 120.65 | 87.3125 | 4 | 19.05
| BST K | 34.1313 | 75.9 | 125 | 95 | 4 | 19.1
| BST R | 34.1313 | 75.9 | 125 | 95 | 4 | 19.1
BS3063 | BST A | 25.4 | 68.2625 | 114.3 | 82.55 | 4 | 14.2875
True Bore | BST D | 25.4 | 68.2625 | 114.3 | 82.55 | 4 | 14.2875
| BST E | 25.4 | 68.2625 | 114.3 | 82.55 | 4 | 14.2875
| BST F | 25.4 | 68.2625 | 120.65 | 87.3125 | 4 | 19.05
| BST H | 25.4 | 68.2625 | 120.65 | 87.3125 | 4 | 19.05
| BST J | 25.4 | 68.2625 | 120.65 | 87.3125 | 4 | 19.05
| BST K | 25.4 | 75.9 | 125 | 95 | 4 | 19.1
| BST R | 25.4 | 75.9 | 125 | 95 | 4 | 19.1
BS EN 1514-1 | PN2.5 | 35 | 63 | 100 | 75 | 4 | 11
& DIN2690 | PN6 | 35 | 63 | 100 | 75 | 4 | 11
| PN10 | 35 | 70 | 115 | 85 | 4 | 14
| PN16 | 35 | 70 | 115 | 85 | 4 | 14
| PN25 | 35 | 70 | 115 | 85 | 4 | 14
| PN40 | 35 | 70 | 115 | 85 | 4 | 14
AS4087 | Class 14/16 | 34.1 | 69 | 115 | 83 | 4 | 14
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 35 | 65 | 95 | 75 | 4 | 12
| 10K | 35 | 74 | 125 | 90 | 4 | 19
| 16K | 35 | 74 | 125 | 90 | 4 | 19
| 20K | 35 | 74 | 125 | 90 | 4 | 19
| 30K | 35 | 79 | 130 | 95 | 4 | 19
| 40K | 35 | 79 | 130 | 95 | 4 | 19
| 63K | 35 | 80 | 140 | 100 | 4 | 23
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | 36 | - | 100 | 75 | 4 | 11
| PN10 | 36 | - | 115 | 85 | 4 | 14
| PN16 | 36 | - | 115 | 85 | 4 | 14
| PN25 | 36 | - | 115 | 85 | 4 | 14
ISO7483 | PN2.5 | 34 | 64 | 100 | 75 | 4 | 11
| PN6 | 34 | 64 | 100 | 75 | 4 | 11
| PN10 | 34 | 71 | 115 | 85 | 4 | 14
| PN16 | 34 | 71 | 115 | 85 | 4 | 14
| PN20 | 34 | 65.5 | 110 | 79.5 | 4 | 16
| PN25 | 34 | 71 | 115 | 85 | 4 | 14
| PN40 | 34 | 71 | 115 | 85 | 4 | 14
| PN50 | 34 | 71 | - | - | - | -
| PN110 | 34 | 71 | - | - | - | -
| PN150 | 34 | 77.5 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 32mm
1-1/4" / 32mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 42.164 | 76.2 | 117.348 | 88.9 | 4 | 15.748
EN12560-1 | ASA150 | 42.164 | 76.2 | 117.348 | 88.9 | 4 | 15.748
Nominal Bore | ASA300 | 42.164 | 82.55 | 133.35 | 98.552 | 4 | 19.05
| ASA600 | 42.164 | 82.55 | 133.35 | 98.552 | 4 | 19.05
ANSI B16.21 & | ASA125 | 31.8 | 76.2 | 117.348 | 88.9 | 4 | 15.748
EN12560-1 | ASA150 | 31.8 | 76.2 | 117.348 | 88.9 | 4 | 15.748
True Bore | ASA300 | 31.8 | 82.55 | 133.35 | 98.552 | 4 | 19.05
| ASA600 | 31.8 | 82.55 | 133.35 | 98.552 | 4 | 19.05
BS3063 | BST A | 42.8625 | 73.025 | 120.65 | 87.3125 | 4 | 14.2875
Nominal Bore | BST D | 42.8625 | 73.025 | 120.65 | 87.3125 | 4 | 14.2875
| BST E | 42.8625 | 73.025 | 120.65 | 87.3125 | 4 | 14.2875
| BST F | 42.8625 | 79.345 | 133.35 | 98.425 | 4 | 19.08
| BST H | 42.8625 | 79.345 | 133.35 | 98.425 | 4 | 19.08
| BST J | 42.8625 | 79.345 | 133.35 | 98.425 | 4 | 19.08
| BST K | 42.8625 | 78.9 | 135 | 98 | 4 | 19.1
| BST R | 42.8625 | 78.9 | 135 | 98 | 4 | 19.1
BS3063 | BST A | 31.8 | 73.025 | 120.65 | 87.3125 | 4 | 14.2875
True Bore | BST D | 31.8 | 73.025 | 120.65 | 87.3125 | 4 | 14.2875
| BST E | 31.8 | 73.025 | 120.65 | 87.3125 | 4 | 14.2875
| BST F | 31.8 | 79.345 | 133.35 | 98.425 | 4 | 19.08
| BST H | 31.8 | 79.345 | 133.35 | 98.425 | 4 | 19.08
| BST J | 31.8 | 79.345 | 133.35 | 98.425 | 4 | 19.08
| BST K | 31.8 | 78.9 | 135 | 98 | 4 | 19.1
| BST R | 31.8 | 78.9 | 135 | 98 | 4 | 19.1
BS EN 1514-1 | PN2.5 | 43 | 75 | 120 | 90 | 4 | 14
& DIN2690 | PN6 | 43 | 75 | 120 | 90 | 4 | 14
| PN10 | 43 | 82 | 140 | 100 | 4 | 18
| PN16 | 43 | 82 | 140 | 100 | 4 | 18
| PN25 | 43 | 82 | 140 | 100 | 4 | 18
| PN40 | 43 | 82 | 140 | 100 | 4 | 18
AS4087 | Class 14/16 | 42.9 | 73 | 120 | 87 | 4 | 14
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 43 | 78 | 115 | 90 | 4 | 15
| 10K | 43 | 84 | 135 | 100 | 4 | 19
| 16K | 43 | 84 | 135 | 100 | 4 | 19
| 20K | 43 | 84 | 135 | 100 | 4 | 19
| 30K | 43 | 89 | 140 | 105 | 4 | 19
| 40K | 43 | 89 | 140 | 105 | 4 | 19
| 63K | 43 | 90 | 150 | 110 | 4 | 23
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | 47 | - | 120 | 90 | 4 | 14
| PN10 | 47 | - | 140 | 100 | 4 | 18
| PN16 | 47 | - | 140 | 100 | 4 | 18
| PN25 | 47 | - | 140 | 100 | 4 | 18
ISO7483 | PN2.5 | 43 | 76 | 120 | 90 | 4 | 14
| PN6 | 43 | 76 | 120 | 90 | 4 | 14
| PN10 | 43 | 82 | 140 | 100 | 4 | 18
| PN16 | 43 | 82 | 140 | 100 | 4 | 18
| PN20 | 43 | 75 | 120 | 89 | 4 | 16
| PN25 | 43 | 82 | 140 | 100 | 4 | 18
| PN40 | 43 | 82 | 140 | 100 | 4 | 18
| PN50 | 43 | 80.5 | - | - | - | -
| PN110 | 43 | 80.5 | - | - | - | -
| PN150 | 43 | 87 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 40mm
1-1/2" / 40mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 48.514 | 85.852 | 127 | 98.552 | 4 | 15.748
EN12560-1 | ASA150 | 48.514 | 85.852 | 127 | 98.552 | 4 | 15.748
Nominal Bore | ASA300 | 48.514 | 95.25 | 155.448 | 114.3 | 4 | 22.352
| ASA600 | 48.514 | 95.25 | 155.448 | 114.3 | 4 | 22.352
ANSI B16.21 & | ASA125 | 38.1 | 85.852 | 127 | 98.552 | 4 | 15.748
EN12560-1 | ASA150 | 38.1 | 85.852 | 127 | 98.552 | 4 | 15.748
True Bore | ASA300 | 38.1 | 95.25 | 155.448 | 114.3 | 4 | 22.352
| ASA600 | 38.1 | 95.25 | 155.448 | 114.3 | 4 | 22.352
BS3063 | BST A | 48.4188 | 84.1375 | 133.35 | 98.425 | 4 | 14.2875
Nominal Bore | BST D | 48.4188 | 84.1375 | 133.35 | 98.425 | 4 | 14.2875
| BST E | 48.4188 | 84.1375 | 133.35 | 98.425 | 4 | 14.2875
| BST F | 48.4188 | 85.725 | 139.7 | 104.775 | 4 | 19.05
| BST H | 48.4188 | 85.725 | 139.7 | 104.775 | 4 | 19.05
| BST J | 48.4188 | 85.725 | 139.7 | 104.775 | 4 | 19.05
| BST K | 48.4188 | 91.8 | 150 | 114 | 4 | 22.2
| BST R | 48.4188 | 91.8 | 150 | 114 | 4 | 22.2
BS3063 | BST A | 38.1 | 84.1375 | 133.35 | 98.425 | 4 | 14.2875
True Bore | BST D | 38.1 | 84.1375 | 133.35 | 98.425 | 4 | 14.2875
| BST E | 38.1 | 84.1375 | 133.35 | 98.425 | 4 | 14.2875
| BST F | 38.1 | 85.725 | 139.7 | 104.775 | 4 | 19.05
| BST H | 38.1 | 85.725 | 139.7 | 104.775 | 4 | 19.05
| BST J | 38.1 | 85.725 | 139.7 | 104.775 | 4 | 19.05
| BST K | 38.1 | 91.8 | 150 | 114 | 4 | 22.2
| BST R | 38.1 | 91.8 | 150 | 114 | 4 | 22.2
BS EN 1514-1 | PN2.5 | 49 | 85 | 130 | 100 | 4 | 14
& DIN2690 | PN6 | 49 | 85 | 130 | 100 | 4 | 14
| PN10 | 49 | 92 | 150 | 110 | 4 | 18
| PN16 | 49 | 92 | 150 | 110 | 4 | 18
| PN25 | 49 | 92 | 150 | 110 | 4 | 18
| PN40 | 49 | 92 | 150 | 110 | 4 | 18
AS4087 | Class 14/16 | 48.4 | 84 | 135 | 98 | 4 | 14
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 49 | 83 | 120 | 95 | 4 | 15
| 10K | 49 | 89 | 140 | 105 | 4 | 19
| 16K | 49 | 89 | 140 | 105 | 4 | 19
| 20K | 49 | 89 | 140 | 105 | 4 | 19
| 30K | 49 | 100 | 160 | 120 | 4 | 23
| 40K | 49 | 100 | 160 | 120 | 4 | 23
| 63K | 49 | 108 | 175 | 130 | 4 | 25
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | 53 | - | 130 | 100 | 4 | 14
| PN10 | 53 | - | 150 | 110 | 4 | 18
| PN16 | 53 | - | 150 | 110 | 4 | 18
| PN25 | 53 | - | 150 | 110 | 4 | 18
ISO7483 | PN2.5 | 49 | 86 | 130 | 100 | 4 | 14
| PN6 | 49 | 86 | 130 | 100 | 4 | 14
| PN10 | 49 | 92 | 150 | 110 | 4 | 18
| PN16 | 49 | 92 | 150 | 110 | 4 | 18
| PN20 | 49 | 84.5 | 130 | 98.5 | 4 | 16
| PN25 | 49 | 92 | 150 | 110 | 4 | 18
| PN40 | 49 | 92 | 150 | 110 | 4 | 18
| PN50 | 49 | 94.5 | - | - | - | -
| PN110 | 49 | 94.5 | - | - | - | -
| PN150 | 49 | 97 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 50mm
2" / 50mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 60.452 | 104.648 | 152.4 | 120.65 | 4 | 19.05
EN12560-1 | ASA150 | 60.452 | 104.648 | 152.4 | 120.65 | 4 | 19.05
Nominal Bore | ASA300 | 60.452 | 111.252 | 165.1 | 127 | 8 | 19.05
| ASA600 | 60.452 | 111.252 | 165.1 | 127 | 8 | 19.05
ANSI B16.21 & | ASA125 | 50.8 | 104.648 | 152.4 | 120.65 | 4 | 19.05
EN12560-1 | ASA150 | 50.8 | 104.648 | 152.4 | 120.65 | 4 | 19.05
True Bore | ASA300 | 50.8 | 111.252 | 165.1 | 127 | 8 | 19.05
| ASA600 | 50.8 | 111.252 | 165.1 | 127 | 8 | 19.05
BS3063 | BST A | 60.325 | 95.25 | 152.4 | 114.3 | 4 | 19.05
Nominal Bore | BST D | 60.325 | 95.25 | 152.4 | 114.3 | 4 | 19.05
| BST E | 60.325 | 95.25 | 152.4 | 114.3 | 4 | 19.05
| BST F | 60.325 | 107.95 | 165.1 | 127 | 4 | 19.05
| BST H | 60.325 | 107.95 | 165.1 | 127 | 4 | 19.05
| BST J | 60.325 | 107.95 | 165.1 | 127 | 4 | 19.05
| BST K | 60.325 | 107.95 | 165.1 | 127 | 8 | 19.05
| BST R | 60.325 | 107.95 | 165.1 | 127 | 8 | 19.05
BS3063 | BST A | 50.8 | 95.25 | 152.4 | 114.3 | 4 | 19.05
True Bore | BST D | 50.8 | 95.25 | 152.4 | 114.3 | 4 | 19.05
| BST E | 50.8 | 95.25 | 152.4 | 114.3 | 4 | 19.05
| BST F | 50.8 | 107.95 | 165.1 | 127 | 4 | 19.05
| BST H | 50.8 | 107.95 | 165.1 | 127 | 4 | 19.05
| BST J | 50.8 | 107.95 | 165.1 | 127 | 4 | 19.05
| BST K | 50.8 | 107.95 | 165.1 | 127 | 8 | 19.05
| BST R | 50.8 | 107.95 | 165.1 | 127 | 8 | 19.05
BS EN 1514-1 | PN2.5 | 61 | 95 | 140 | 110 | 4 | 14
& DIN2690 | PN6 | 61 | 95 | 140 | 110 | 4 | 14
| PN10 | 61 | 107 | 165 | 125 | 4 | 18
| PN16 | 61 | 107 | 165 | 125 | 4 | 18
| PN25 | 61 | 107 | 165 | 125 | 4 | 18
| PN40 | 61 | 107 | 165 | 125 | 4 | 18
AS4087 | Class 14/16 | 60.3 | 96 | 150 | 114 | 4 | 18
| Class 21/35 | 60.3 | 109 | 165 | 127 | 4 | 18
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 61 | 93 | 130 | 105 | 4 | 15
| 10K | 61 | 104 | 155 | 120 | 4 | 19
| 16K | 61 | 104 | 155 | 120 | 8 | 19
| 20K | 61 | 104 | 155 | 120 | 8 | 19
| 30K | 61 | 114 | 165 | 130 | 8 | 19
| 40K | 61 | 114 | 165 | 130 | 8 | 19
| 63K | 61 | 125 | 185 | 145 | 8 | 23
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | 65 | - | 140 | 110 | 4 | 14
| PN10 | 65 | - | 165 | 125 | 4 | 18
| PN16 | 65 | - | 165 | 125 | 4 | 18
| PN25 | 65 | - | 165 | 125 | 4 | 18
ISO7483 | PN2.5 | 61 | 96 | 140 | 110 | 4 | 14
| PN6 | 61 | 96 | 140 | 110 | 4 | 14
| PN10 | 61 | 107 | 165 | 125 | 4 | 18
| PN16 | 61 | 107 | 165 | 125 | 4 | 18
| PN20 | 61 | 102.5 | 150 | 120.5 | 4 | 20
| PN25 | 61 | 107 | 165 | 125 | 4 | 18
| PN40 | 61 | 107 | 165 | 125 | 4 | 18
| PN50 | 61 | 109 | - | - | - | -
| PN110 | 61 | 109 | - | - | - | -
| PN150 | 61 | 141 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 65mm
2-1/2" / 65mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 73.152 | 123.952 | 177.8 | 139.7 | 4 | 19.05
EN12560-1 | ASA150 | 73.152 | 123.952 | 177.8 | 139.7 | 4 | 19.05
Nominal Bore | ASA300 | 73.152 | 130.048 | 190.5 | 149.352 | 8 | 22.352
| ASA600 | 73.152 | 130.048 | 190.5 | 149.352 | 8 | 22.352
ANSI B16.21 & | ASA125 | 63.5 | 123.952 | 177.8 | 139.7 | 4 | 19.05
EN12560-1 | ASA150 | 63.5 | 123.952 | 177.8 | 139.7 | 4 | 19.05
True Bore | ASA300 | 63.5 | 130.048 | 190.5 | 149.352 | 8 | 22.352
| ASA600 | 63.5 | 130.048 | 190.5 | 149.352 | 8 | 22.352
BS3063 | BST A | 76.2 | 107.95 | 165.1 | 127 | 4 | 19.05
Nominal Bore | BST D | 76.2 | 107.95 | 165.1 | 127 | 4 | 19.05
| BST E | 76.2 | 107.95 | 165.1 | 127 | 4 | 19.05
| BST F | 76.2 | 127 | 184.15 | 146.05 | 8 | 19.05
| BST H | 76.2 | 127 | 184.15 | 146.05 | 8 | 19.05
| BST J | 76.2 | 127 | 184.15 | 146.05 | 8 | 19.05
| BST K | 76.2 | 123.85 | 184.15 | 146.05 | 8 | 22.2
| BST R | 76.2 | 123.85 | 184.15 | 146.05 | 8 | 22.2
BS3063 | BST A | 63.5 | 107.95 | 165.1 | 127 | 4 | 19.05
True Bore | BST D | 63.5 | 107.95 | 165.1 | 127 | 4 | 19.05
| BST E | 63.5 | 107.95 | 165.1 | 127 | 4 | 19.05
| BST F | 63.5 | 127 | 184.15 | 146.05 | 8 | 19.05
| BST H | 63.5 | 127 | 184.15 | 146.05 | 8 | 19.05
| BST J | 63.5 | 127 | 184.15 | 146.05 | 8 | 19.05
| BST K | 63.5 | 123.85 | 184.15 | 146.05 | 8 | 22.2
| BST R | 63.5 | 123.85 | 184.15 | 146.05 | 8 | 22.2
BS EN 1514-1 | PN2.5 | 77 | 115 | 160 | 130 | 4 | 14
& DIN2690 | PN6 | 77 | 115 | 160 | 130 | 4 | 14
| PN10 | 77 | 127 | 185 | 145 | 4 | 18
| PN16 | 77 | 127 | 185 | 145 | 4 | 18
| PN25 | 77 | 127 | 185 | 145 | 8 | 18
| PN40 | 77 | 127 | 185 | 145 | 8 | 18
AS4087 | Class 14/16 | 76.2 | 109 | 165 | 127 | 4 | 18
| Class 21/35 | 76.2 | 128 | 185 | 146 | 8 | 18
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 77 | 118 | 155 | 130 | 4 | 15
| 10K | 77 | 124 | 175 | 140 | 4 | 19
| 16K | 77 | 124 | 175 | 140 | 8 | 19
| 20K | 77 | 124 | 175 | 140 | 8 | 19
| 30K | 77 | 140 | 200 | 160 | 8 | 23
| 40K | 77 | 140 | 200 | 160 | 8 | 23
| 63K | 77 | 153 |  | 175 | 8 | 25
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | 81 | - | 160 | 130 | 4 | 14
| PN10 | 81 | - | 185 | 145 | 4 | 18
| PN16 | 81 | - | 185 | 145 | 4 | 18
| PN25 | 81 | - | 185 | 145 | 4 | 18
ISO7483 | PN2.5 | 77 | 116 | 160 | 130 | 4 | 14
| PN6 | 77 | 116 | 160 | 130 | 4 | 14
| PN10 | 77 | 127 | 185 | 145 | 8 | 18
| PN16 | 77 | 127 | 185 | 145 | 8 | 18
| PN20 | 73 | 121.5 | 180 | 139.5 | 4 | 20
| PN25 | 77 | 127 | 185 | 145 | 8 | 18
| PN40 | 77 | 127 | 185 | 145 | 8 | 18
| PN50 | 73 | 129 | - | - | - | -
| PN110 | 73 | 129 | - | - | - | -
| PN150 | 73 | 163.5 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 80mm
3" / 80mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 88.9 | 136.652 | 190.5 | 152.4 | 4 | 19.05
EN12560-1 | ASA150 | 88.9 | 136.652 | 190.5 | 152.4 | 4 | 19.05
Nominal Bore | ASA300 | 88.9 | 149.352 | 209.55 | 168.148 | 8 | 22.352
| ASA600 | 88.9 | 149.352 | 209.55 | 168.148 | 8 | 22.352
ANSI B16.21 & | ASA125 | 76.2 | 136.652 | 190.5 | 152.4 | 4 | 19.05
EN12560-1 | ASA150 | 76.2 | 136.652 | 190.5 | 152.4 | 4 | 19.05
True Bore | ASA300 | 76.2 | 149.352 | 209.55 | 168.148 | 8 | 22.352
| ASA600 | 76.2 | 149.352 | 209.55 | 168.148 | 8 | 22.352
BS3063 | BST A | 88.9 | 127 | 184.15 | 146.05 | 4 | 19.05
Nominal Bore | BST D | 88.9 | 127 | 184.15 | 146.05 | 4 | 19.05
| BST E | 88.9 | 127 | 184.15 | 146.05 | 4 | 19.05
| BST F | 88.9 | 146.05 | 203.2 | 165.1 | 8 | 19.05
| BST H | 88.9 | 146.05 | 203.2 | 165.1 | 8 | 19.05
| BST J | 88.9 | 142.9 | 203.2 | 165.1 | 8 | 22.2
| BST K | 88.9 | 142.9 | 203.2 | 165.1 | 8 | 22.2
| BST R | 88.9 | 142.9 | 203.2 | 165.1 | 8 | 22.2
BS3063 | BST A | 76.2 | 127 | 184.15 | 146.05 | 4 | 19.05
True Bore | BST D | 76.2 | 127 | 184.15 | 146.05 | 4 | 19.05
| BST E | 76.2 | 127 | 184.15 | 146.05 | 4 | 19.05
| BST F | 76.2 | 146.05 | 203.2 | 165.1 | 8 | 19.05
| BST H | 76.2 | 146.05 | 203.2 | 165.1 | 8 | 19.05
| BST J | 76.2 | 142.9 | 203.2 | 165.1 | 8 | 22.2
| BST K | 76.2 | 142.9 | 203.2 | 165.1 | 8 | 22.2
| BST R | 76.2 | 142.9 | 203.2 | 165.1 | 8 | 22.2
BS EN 1514-1 | PN2.5 | 90 | 132 | 190 | 150 | 4 | 18
& DIN2690 | PN6 | 90 | 132 | 190 | 150 | 4 | 18
| PN10 | 90 | 142 | 200 | 160 | 8 | 18
| PN16 | 90 | 142 | 200 | 160 | 8 | 18
| PN25 | 90 | 142 | 200 | 160 | 8 | 18
| PN40 | 90 | 142 | 200 | 160 | 8 | 18
AS4087 | Class 14/16 | 88.9 | 128 | 185 | 146 | 4 | 18
| Class 21/35 | 88.9 | 147 | 205 | 165 | 8 | 18
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 90 | 129 | 180 | 145 | 4 | 19
| 10K | 90 | 134 | 185 | 150 | 8 | 19
| 16K | 90 | 140 | 200 | 160 | 8 | 23
| 20K | 90 | 140 |  | 160 | 8 | 23
| 30K | 90 | 150 | 210 | 170 | 8 | 23
| 40K | 90 | 150 | 210 | 170 | 8 | 23
| 63K | 90 | 163 | 230 | 185 | 8 | 25
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | 93 | - | 190 | 150 | 4 | 18
| PN10 | 93 | - | 200 | 160 | 8 | 18
| PN16 | 93 | - | 200 | 160 | 8 | 18
| PN25 | 93 | - | 200 | 160 | 8 | 18
ISO7483 | PN2.5 | 89 | 132 | 190 | 150 | 4 | 18
| PN6 | 89 | 132 | 190 | 150 | 4 | 18
| PN10 | 89 | 142 | 200 | 160 | 8 | 18
| PN16 | 89 | 142 | 200 | 160 | 8 | 18
| PN20 | 89 | 134.5 | 190 | 152.5 | 4 | 20
| PN25 | 89 | 142 | 200 | 160 | 8 | 18
| PN40 | 89 | 142 | 200 | 160 | 8 | 18
| PN50 | 89 | 148.5 | - | - | - | -
| PN110 | 89 | 148.5 | - | - | - | -
| PN150 | 89 | 166.5 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 90mm
3-1/2" / 90mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 101.6 | 162.052 | 215.9 | 177.8 | 8 | 19.05
EN12560-1 | ASA150 | 101.6 | 162.052 | 215.9 | 177.8 | 8 | 19.05
Nominal Bore | ASA300 | 101.6 | 165.1 | 228.6 | 184.15 | 8 | 22.352
| ASA600 | 101.6 | 162.052 | 228.6 | 184.15 | 8 | 25.4
ANSI B16.21 & | ASA125 | 88.9 | 162.052 | 215.9 | 177.8 | 8 | 19.05
EN12560-1 | ASA150 | 88.9 | 162.052 | 215.9 | 177.8 | 8 | 19.05
True Bore | ASA300 | 88.9 | 165.1 | 228.6 | 184.15 | 8 | 22.352
| ASA600 | 88.9 | 162.052 | 228.6 | 184.15 | 8 | 25.4
BS3063 | BST A | 101.6 | 146.05 | 203.2 | 165.1 | 4 | 19.05
Nominal Bore | BST D | 101.6 | 146.05 | 203.2 | 165.1 | 4 | 19.05
| BST E | 101.6 | 146.05 | 203.2 | 165.1 | 8 | 19.05
| BST F | 101.6 | 158.75 | 215.9 | 177.8 | 8 | 19.05
| BST H | 101.6 | 158.75 | 215.9 | 177.8 | 8 | 19.05
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 88.9 | 146.05 | 203.2 | 165.1 | 4 | 19.05
True Bore | BST D | 88.9 | 146.05 | 203.2 | 165.1 | 4 | 19.05
| BST E | 88.9 | 146.05 | 203.2 | 165.1 | 8 | 19.05
| BST F | 88.9 | 158.75 | 215.9 | 177.8 | 8 | 19.05
| BST H | 88.9 | 158.75 | 215.9 | 177.8 | 8 | 19.05
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 102 | 139 | 190 | 155 | 4 | 19
| 10K | 102 | 144 | 195 | 160 | 8 | 19
| 16K | 102 | 150 | 210 | 170 | 8 | 23
| 20K | 102 | 150 | 210 | 170 | 8 | 23
| 30K | 102 | 163 | 230 | 185 | 8 | 25
| 40K | 102 | 163 | 230 | 185 | 8 | 25
| 63K | 102 | 181 | 255 | 205 | 8 | 27
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | - | - | - | - | - | -
| PN110 | - | - | - | - | - | -
| PN150 | - | - | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 100mm
4" / 100mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 114.3 | 174.752 | 228.6 | 190.5 | 8 | 19.05
EN12560-1 | ASA150 | 114.3 | 174.752 | 228.6 | 190.5 | 8 | 19.05
Nominal Bore | ASA300 | 114.3 | 180.848 | 254 | 200.152 | 8 | 22.352
| ASA600 | 114.3 | 193.548 | 273.05 | 215.9 | 8 | 25.4
ANSI B16.21 & | ASA125 | 101.6 | 174.752 | 228.6 | 190.5 | 8 | 19.05
EN12560-1 | ASA150 | 101.6 | 174.752 | 228.6 | 190.5 | 8 | 19.05
True Bore | ASA300 | 101.6 | 180.848 | 254 | 200.152 | 8 | 22.352
| ASA600 | 101.6 | 193.548 | 273.05 | 215.9 | 8 | 25.4
BS3063 | BST A | 114.3 | 158.75 | 215.9 | 177.8 | 4 | 19.05
Nominal Bore | BST D | 114.3 | 158.75 | 215.9 | 177.8 | 4 | 19.05
| BST E | 114.3 | 158.75 | 215.9 | 177.8 | 8 | 19.05
| BST F | 114.3 | 171.45 | 228.6 | 190.5 | 8 | 19.05
| BST H | 114.3 | 171.45 | 228.6 | 190.5 | 8 | 19.05
| BST J | 114.3 | 168.3 | 228.6 | 190.5 | 8 | 22.2
| BST K | 114.3 | 171 | 240 | 197 | 8 | 26
| BST R | 114.3 | 171 | 240 | 197 | 8 | 26
BS3063 | BST A | 101.6 | 158.75 | 215.9 | 177.8 | 4 | 19.05
True Bore | BST D | 101.6 | 158.75 | 215.9 | 177.8 | 4 | 19.05
| BST E | 101.6 | 158.75 | 215.9 | 177.8 | 8 | 19.05
| BST F | 101.6 | 171.45 | 228.6 | 190.5 | 8 | 19.05
| BST H | 101.6 | 171.45 | 228.6 | 190.5 | 8 | 19.05
| BST J | 101.6 | 168.3 | 228.6 | 190.5 | 8 | 22.2
| BST K | 101.6 | 171 | 240 | 197 | 8 | 26
| BST R | 101.6 | 171 | 240 | 197 | 8 | 26
BS EN 1514-1 | PN2.5 | 115 | 152 | 210 | 170 | 4 | 18
& DIN2690 | PN6 | 115 | 152 | 210 | 170 | 4 | 18
| PN10 | 115 | 162 | 220 | 180 | 8 | 18
| PN16 | 115 | 162 | 220 | 180 | 8 | 18
| PN25 | 115 | 168 | 235 | 190 | 8 | 22
| PN40 | 115 | 168 | 235 | 190 | 8 | 22
AS4087 | Class 14/16 | 114.3 | 160 | 215 | 178 | 4 | 18
| Class 21/35 | 114.3 | 173 | 230 | 191 | 8 | 18
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 115 | 149 | 200 | 165 | 8 | 19
| 10K | 115 | 159 | 210 | 175 | 8 | 19
| 16K | 115 | 165 | 225 | 185 | 8 | 23
| 20K | 115 | 165 | 225 | 185 | 8 | 23
| 30K | 115 | 173 | 240 | 195 | 8 | 25
| 40K | 115 | 183 | 250 | 205 | 8 | 25
| 63K | 115 | 196 | 270 | 220 | 8 | 27
AWWA C207-01 | Class B | 116.078 | 173 | 228.6 | 190.5 | 8 | 19.05
| Class D | 116.078 | 173 | 228.6 | 190.5 | 8 | 19.05
| Class E | 116.078 | 173 | 228.6 | 190.5 | 8 | 19.05
| Class F | 116.078 | 179.5 | 254 | 200.152 | 8 | 22.225
DIN 86071 | PN6 | 120 | - | 210 | 170 | 4 | 18
| PN10 | 120 | - | 220 | 180 | 8 | 18
| PN16 | 120 | - | 220 | 180 | 8 | 18
| PN25 | 120 | - | 235 | 190 | 8 | 22
ISO7483 | PN2.5 | 115 | 152 | 210 | 170 | 4 | 18
| PN6 | 115 | 152 | 210 | 170 | 4 | 18
| PN10 | 115 | 162 | 220 | 180 | 8 | 18
| PN16 | 115 | 162 | 220 | 180 | 8 | 18
| PN20 | 115 | 172.5 | 230 | 190.5 | 8 | 20
| PN25 | 115 | 168 | 235 | 190 | 8 | 22
| PN40 | 115 | 168 | 235 | 190 | 8 | 22
| PN50 | 115 | 180 | - | - | - | -
| PN110 | 115 | 192 | - | - | - | -
| PN150 | 115 | 205 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 125mm
5" / 125mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 141.224 | 196.85 | 254 | 215.9 | 8 | 22.352
EN12560-1 | ASA150 | 141.224 | 196.85 | 254 | 215.9 | 8 | 22.352
Nominal Bore | ASA300 | 141.224 | 215.9 | 279.4 | 234.95 | 8 | 22.352
| ASA600 | 141.224 | 241.3 | 330.2 | 266.7 | 8 | 28.448
ANSI B16.21 & | ASA125 | 127 | 196.85 | 254 | 215.9 | 8 | 22.352
EN12560-1 | ASA150 | 127 | 196.85 | 254 | 215.9 | 8 | 22.352
True Bore | ASA300 | 127 | 215.9 | 279.4 | 234.95 | 8 | 22.352
| ASA600 | 127 | 241.3 | 330.2 | 266.7 | 8 | 28.448
BS3063 | BST A | 139.7 | 190.5 | 254 | 209.55 | 4 | 19.05
Nominal Bore | BST D | 139.7 | 190.5 | 254 | 209.55 | 8 | 19.05
| BST E | 139.7 | 190.5 | 254 | 209.55 | 8 | 19.05
| BST F | 139.7 | 212.725 | 279.4 | 234.95 | 8 | 22.225
| BST H | 139.7 | 212.725 | 279.4 | 234.95 | 8 | 22.225
| BST J | 139.7 | 208.95 | 279.4 | 234.95 | 8 | 26
| BST K | 139.7 | 208.95 | 279.4 | 234.95 | 12 | 26
| BST R | 139.7 | 208.95 | 279.4 | 234.95 | 12 | 26
BS3063 | BST A | 127 | 190.5 | 254 | 209.55 | 4 | 19.05
True Bore | BST D | 127 | 190.5 | 254 | 209.55 | 8 | 19.05
| BST E | 127 | 190.5 | 254 | 209.55 | 8 | 19.05
| BST F | 127 | 212.725 | 279.4 | 234.95 | 8 | 22.225
| BST H | 127 | 212.725 | 279.4 | 234.95 | 8 | 22.225
| BST J | 127 | 208.95 | 279.4 | 234.95 | 8 | 26
| BST K | 127 | 208.95 | 279.4 | 234.95 | 12 | 26
| BST R | 127 | 208.95 | 279.4 | 234.95 | 12 | 26
BS EN 1514-1 | PN2.5 | 141 | 182 | 240 | 200 | 8 | 18
& DIN2690 | PN6 | 141 | 182 | 240 | 200 | 8 | 18
| PN10 | 141 | 192 | 250 | 210 | 8 | 18
| PN16 | 141 | 192 | 250 | 210 | 8 | 18
| PN25 | 141 | 195 | 270 | 220 | 8 | 26
| PN40 | 141 | 195 | 270 | 220 | 8 | 26
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 141 | 184 | 235 | 200 | 8 | 19
| 10K | 141 | 190 | 250 | 210 | 8 | 23
| 16K | 141 | 203 | 270 | 225 | 8 | 25
| 20K | 141 | 203 | 270 | 225 | 8 | 25
| 30K | 141 | 208 | 275 | 230 | 8 | 25
| 40K | 141 | 226 | 300 | 250 | 8 | 27
| 63K | 141 | 235 |  | 265 | 8 | 33
AWWA C207-01 | Class B | 143.764 | 195.3 | 254 | 215.9 | 8 | 22.225
| Class D | 143.764 | 195.3 | 254 | 215.9 | 8 | 22.225
| Class E | 143.764 | 195.3 | 254 | 215.9 | 8 | 22.225
| Class F | 143.764 | 214.3 | 279.4 | 234.95 | 8 | 22.225
DIN 86071 | PN6 | 146 | - | 240 | 200 | 8 | 18
| PN10 | 146 | - | 250 | 210 | 8 | 18
| PN16 | 146 | - | 250 | 210 | 8 | 18
| PN25 | 146 | - | 270 | 220 | 8 | 26
ISO7483 | PN2.5 | 141 | 182 | 240 | 200 | 8 | 18
| PN6 | 141 | 182 | 240 | 200 | 8 | 18
| PN10 | 141 | 192 | 250 | 210 | 8 | 18
| PN16 | 141 | 192 | 250 | 210 | 8 | 18
| PN20 | 141 | 196 | 255 | 216 | 8 | 22
| PN25 | 141 | 194 | 270 | 220 | 8 | 26
| PN40 | 141 | 194 | 270 | 220 | 8 | 26
| PN50 | 141 | 215 | - | - | - | -
| PN110 | 141 | 240 | - | - | - | -
| PN150 | 141 | 246.5 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 150mm
6" / 150mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 168.148 | 222.25 | 279.4 | 241.3 | 8 | 22.352
EN12560-1 | ASA150 | 168.148 | 222.25 | 279.4 | 241.3 | 8 | 22.352
Nominal Bore | ASA300 | 168.148 | 250.952 | 317.5 | 269.748 | 12 | 22.352
| ASA600 | 168.148 | 266.7 | 355.6 | 292.1 | 12 | 28.448
ANSI B16.21 & | ASA125 | 152.4 | 222.25 | 279.4 | 241.3 | 8 | 22.352
EN12560-1 | ASA150 | 152.4 | 222.25 | 279.4 | 241.3 | 8 | 22.352
True Bore | ASA300 | 152.4 | 250.952 | 317.5 | 269.748 | 12 | 22.352
| ASA600 | 152.4 | 266.7 | 355.6 | 292.1 | 12 | 28.448
BS3063 | BST A | 168.275 | 215.9 | 279.4 | 234.95 | 8 | 19.05
Nominal Bore | BST D | 168.275 | 215.9 | 279.4 | 234.95 | 8 | 19.05
| BST E | 168.275 | 212.725 | 279.4 | 234.95 | 8 | 22.225
| BST F | 168.275 | 238.125 | 304.8 | 260.35 | 12 | 22.225
| BST H | 168.275 | 238.125 | 304.8 | 260.35 | 12 | 22.225
| BST J | 168.275 | 234.35 | 304.8 | 260.35 | 12 | 26
| BST K | 168.275 | 234.35 | 304.8 | 260.35 | 12 | 26
| BST R | 168.275 | 234.35 | 304.8 | 260.35 | 12 | 26
BS3063 | BST A | 152.4 | 215.9 | 279.4 | 234.95 | 8 | 19.05
True Bore | BST D | 152.4 | 215.9 | 279.4 | 234.95 | 8 | 19.05
| BST E | 152.4 | 212.725 | 279.4 | 234.95 | 8 | 22.225
| BST F | 152.4 | 238.125 | 304.8 | 260.35 | 12 | 22.225
| BST H | 152.4 | 238.125 | 304.8 | 260.35 | 12 | 22.225
| BST J | 152.4 | 234.35 | 304.8 | 260.35 | 12 | 26
| BST K | 152.4 | 234.35 | 304.8 | 260.35 | 12 | 26
| BST R | 152.4 | 234.35 | 304.8 | 260.35 | 12 | 26
BS EN 1514-1 | PN2.5 | 169 | 207 | 265 | 225 | 8 | 18
& DIN2690 | PN6 | 169 | 207 | 265 | 225 | 8 | 18
| PN10 | 169 | 218 | 285 | 240 | 8 | 22
| PN16 | 169 | 218 | 285 | 240 | 8 | 22
| PN25 | 169 | 225 | 300 | 250 | 8 | 26
| PN40 | 169 | 225 | 300 | 250 | 8 | 26
AS4087 | Class 14/16 | 168.3 | 217 | 280 | 235 | 8 | 18
| Class 21/35 | 168.3 | 238 | 305 | 260 | 12 | 22
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 167 | 214 | 265 | 230 | 8 | 19
| 10K | 167 | 220 | 280 | 240 | 8 | 23
| 16K | 167 | 238 | 305 | 260 | 12 | 25
| 20K | 167 | 238 | 305 | 260 | 12 | 25
| 30K | 167 | 251 | 325 | 275 | 12 | 27
| 40K | 167 | 265 | 355 | 295 | 12 | 33
| 63K | 167 | 275 | 365 | 305 | 12 | 33
AWWA C207-01 | Class B | 170.688 | 220.7 | 279.4 | 241.3 | 8 | 22.225
| Class D | 170.688 | 220.7 | 279.4 | 241.3 | 8 | 22.225
| Class E | 170.688 | 220.7 | 279.4 | 241.3 | 8 | 22.225
| Class F | 170.942 | 249.1 | 317.5 | 269.748 | 12 | 22.225
DIN 86071 | PN6 | 172 | - | 265 | 225 | 8 | 18
| PN10 | 172 | - | 285 | 240 | 8 | 22
| PN16 | 172 | - | 285 | 240 | 8 | 22
| PN25 | 172 | - | 300 | 250 | 8 | 26
ISO7483 | PN2.5 | 169 | 207 | 265 | 225 | 8 | 18
| PN6 | 169 | 207 | 265 | 225 | 8 | 18
| PN10 | 169 | 218 | 285 | 240 | 8 | 22
| PN16 | 169 | 218 | 285 | 240 | 8 | 22
| PN20 | 169 | 221.5 | 280 | 241.5 | 8 | 22
| PN25 | 169 | 224 | 300 | 250 | 8 | 26
| PN40 | 169 | 224 | 300 | 250 | 8 | 26
| PN50 | 169 | 250 | - | - | - | -
| PN110 | 169 | 265 | - | - | - | -
| PN150 | 169 | 287.5 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 175mm
7" / 175mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | - | - | - | - | - | -
EN12560-1 | ASA150 | - | - | - | - | - | -
Nominal Bore | ASA300 | - | - | - | - | - | -
| ASA600 | - | - | - | - | - | -
ANSI B16.21 & | ASA125 | - | - | - | - | - | -
EN12560-1 | ASA150 | - | - | - | - | - | -
True Bore | ASA300 | - | - | - | - | - | -
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | 193.7 | 241.3 | 304.8 | 260.4 | 8 | 19.1
Nominal Bore | BST D | 193.7 | 241.3 | 304.8 | 260.35 | 8 | 19.05
| BST E | 193.7 | 238.125 | 304.8 | 260.35 | 8 | 22.225
| BST F | 193.7 | 269.875 | 336.55 | 292.1 | 12 | 22.225
| BST H | 193.7 | 269.875 | 336.55 | 292.1 | 12 | 22.225
| BST J | 193.7 | 266.7 | 336.6 | 292.1 | 12 | 25.4
| BST K | 190.5 | 263.5 | 342.9 | 292.1 | 12 | 28.6
| BST R | - | - | - | - | - | -
BS3063 | BST A | 177.8 | 241.3 | 304.8 | 260.4 | 8 | 19.1
True Bore | BST D | 177.8 | 241.3 | 304.8 | 260.35 | 8 | 19.05
| BST E | 177.8 | 238.125 | 304.8 | 260.35 | 8 | 22.225
| BST F | 177.8 | 269.875 | 336.55 | 292.1 | 12 | 22.225
| BST H | 177.8 | 269.875 | 336.55 | 292.1 | 12 | 22.225
| BST J | 177.8 | 266.7 | 336.6 | 292.1 | 12 | 25.4
| BST K | 177.8 | 263.5 | 342.9 | 292.1 | 12 | 28.6
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | 195 | 237 | - | - | - | -
& DIN2690 | PN6 | 195 | 237 | - | - | - | -
| PN10 | 195 | 248 | 315 | 270 | 8 | 22
| PN16 | 195 | 248 | 315 | 270 | 8 | 22
| PN25 | 195 | 255 | 330 | 280 | 12 | 26
| PN40 | 195 | 267 | 350 | 295 | 12 | 30
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 192 | 240 | 300 | 260 | 8 | 23
| 10K | 192 | 245 | 305 | 265 | 12 | 23
| 16K | - | - | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | 200 | - | 295 | 255 | 8 | 18
| PN10 | 200 | - | 315 | 270 | 8 | 22
| PN16 | 200 | - | 315 | 270 | 8 | 22
| PN25 | 200 | - | 330 | 280 | 12 | 26
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | - | - | - | - | - | -
| PN110 | - | - | - | - | - | -
| PN150 | - | - | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 200mm
8" / 200mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 218.948 | 279.4 | 342.9 | 298.45 | 8 | 22.352
EN12560-1 | ASA150 | 218.948 | 279.4 | 342.9 | 298.45 | 8 | 22.352
Nominal Bore | ASA300 | 218.948 | 307.848 | 381 | 330.2 | 12 | 25.4
| ASA600 | 218.948 | 320.548 | 420.37 | 349.25 | 12 | 31.75
ANSI B16.21 & | ASA125 | 203.2 | 279.4 | 342.9 | 298.45 | 8 | 22.352
EN12560-1 | ASA150 | 203.2 | 279.4 | 342.9 | 298.45 | 8 | 22.352
True Bore | ASA300 | 203.2 | 307.848 | 381 | 330.2 | 12 | 25.4
| ASA600 | 203.2 | 320.548 | 420.37 | 349.25 | 12 | 31.75
BS3063 | BST A | 219.075 | 273.05 | 336.55 | 292.1 | 8 | 19.05
Nominal Bore | BST D | 219.075 | 273.05 | 336.55 | 292.1 | 8 | 19.05
| BST E | 219.075 | 269.875 | 336.55 | 292.1 | 8 | 22.225
| BST F | 219.075 | 301.625 | 368.3 | 323.85 | 12 | 22.225
| BST H | 219.075 | 301.625 | 368.3 | 323.85 | 12 | 22.225
| BST J | 219.075 | 297.85 | 368.3 | 323.85 | 12 | 26
| BST K | 219.075 | 288 | 368.3 | 318 | 12 | 30
| BST R | 219.075 | 294 | 368.3 | 324 | 12 | 30
BS3063 | BST A | 203.2 | 273.05 | 336.55 | 292.1 | 8 | 19.05
True Bore | BST D | 203.2 | 273.05 | 336.55 | 292.1 | 8 | 19.05
| BST E | 203.2 | 269.875 | 336.55 | 292.1 | 8 | 22.225
| BST F | 203.2 | 301.625 | 368.3 | 323.85 | 12 | 22.225
| BST H | 203.2 | 301.625 | 368.3 | 323.85 | 12 | 22.225
| BST J | 203.2 | 297.85 | 368.3 | 323.85 | 12 | 26
| BST K | 203.2 | 288 | 368.3 | 318 | 12 | 30
| BST R | 203.2 | 294 | 368.3 | 324 | 12 | 30
BS EN 1514-1 | PN2.5 | 220 | 262 | 320 | 280 | 8 | 18
& DIN2690 | PN6 | 220 | 262 | 320 | 280 | 8 | 18
| PN10 | 220 | 273 | 340 | 295 | 8 | 22
| PN16 | 220 | 273 | 340 | 295 | 12 | 22
| PN25 | 220 | 285 | 360 | 310 | 12 | 26
| PN40 | 220 | 292 | 375 | 320 | 12 | 30
AS4087 | Class 14/16 | 219.1 | 274 | 335 | 292 | 8 | 18
| Class 21/35 | 219.1 | 302 | 370 | 324 | 12 | 22
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 218 | 260 | 320 | 280 | 8 | 23
| 10K | 218 | 270 | 330 | 290 | 12 | 23
| 16K | 218 | 283 | 350 | 305 | 12 | 25
| 20K | 218 | 283 | 350 | 305 | 12 | 25
| 30K | 218 | 296 | 370 | 320 | 12 | 27
| 40K | 218 | 315 | 405 | 345 | 12 | 33
| 63K | 218 | 330 | 425 | 360 | 12 | 33
AWWA C207-01 | Class B | 221.488 | 277.8 | 342.9 | 298.45 | 8 | 22.225
| Class D | 221.488 | 277.8 | 342.9 | 298.45 | 8 | 22.225
| Class E | 221.488 | 277.8 | 342.9 | 298.45 | 8 | 22.225
| Class F | 221.742 | 306.4 | 381 | 330.2 | 12 | 25.4
DIN 86071 | PN6 | 225 | - | 320 | 280 | 8 | 18
| PN10 | 225 | - | 340 | 295 | 8 | 22
| PN16 | 225 | - | 340 | 295 | 12 | 22
| PN25 | 225 | - | 360 | 310 | 12 | 26
ISO7483 | PN2.5 | 220 | 262 | 320 | 280 | 8 | 18
| PN6 | 220 | 262 | 320 | 280 | 8 | 18
| PN10 | 220 | 273 | 340 | 295 | 8 | 22
| PN16 | 220 | 273 | 340 | 295 | 12 | 22
| PN20 | 220 | 278.5 | 345 | 298.5 | 8 | 22
| PN25 | 220 | 284 | 360 | 310 | 12 | 26
| PN40 | 220 | 290 | 375 | 320 | 12 | 30
| PN50 | 220 | 306 | - | - | - | -
| PN110 | 220 | 319 | - | - | - | -
| PN150 | 220 | 357.5 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 250mm
10" / 250mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 273.05 | 339.852 | 406.4 | 361.95 | 12 | 25.4
EN12560-1 | ASA150 | 273.05 | 339.852 | 406.4 | 361.95 | 12 | 25.4
Nominal Bore | ASA300 | 273.05 | 361.95 | 444.5 | 387.35 | 16 | 28.448
| ASA600 | 273.05 | 400.05 | 508 | 431.8 | 16 | 35.1
ANSI B16.21 & | ASA125 | 254 | 339.852 | 406.4 | 361.95 | 12 | 25.4
EN12560-1 | ASA150 | 254 | 339.852 | 406.4 | 361.95 | 12 | 25.4
True Bore | ASA300 | 254 | 361.95 | 444.5 | 387.35 | 16 | 28.448
| ASA600 | 254 | 400.05 | 508 | 431.8 | 16 | 35.1
BS3063 | BST A | 273.05 | 333.375 | 406.4 | 355.6 | 8 | 22.225
Nominal Bore | BST D | 273.05 | 333.375 | 406.4 | 355.6 | 8 | 22.225
| BST E | 273.05 | 333.375 | 406.4 | 355.6 | 12 | 22.225
| BST F | 273.05 | 355 | 431.8 | 381 | 12 | 26
| BST H | 273.05 | 355 | 431.8 | 381 | 12 | 26
| BST J | 273.05 | 351 | 431.8 | 381 | 12 | 30
| BST K | 273.05 | 351 | 431.8 | 381 | 16 | 30
| BST R | 273.05 | 357 | 431.8 | 387 | 16 | 30
BS3063 | BST A | 254 | 333.375 | 406.4 | 355.6 | 8 | 22.225
True Bore | BST D | 254 | 333.375 | 406.4 | 355.6 | 8 | 22.225
| BST E | 254 | 333.375 | 406.4 | 355.6 | 12 | 22.225
| BST F | 254 | 355 | 431.8 | 381 | 12 | 26
| BST H | 254 | 355 | 431.8 | 381 | 12 | 26
| BST J | 254 | 351 | 431.8 | 381 | 12 | 30
| BST K | 254 | 351 | 431.8 | 381 | 16 | 30
| BST R | 254 | 357 | 431.8 | 387 | 16 | 30
BS EN 1514-1 | PN2.5 | 274 | 318 | 375 | 335 | 12 | 18
& DIN2690 | PN6 | 274 | 318 | 375 | 335 | 12 | 18
| PN10 | 274 | 328 | 395 | 350 | 12 | 22
| PN16 | 274 | 330 | 405 | 355 | 12 | 26
| PN25 | 274 | 342 | 425 | 370 | 12 | 30
| PN40 | 274 | 353 | 450 | 385 | 12 | 33
AS4087 | Class 14/16 | 273.1 | 334 | 405 | 356 | 8 | 22
| Class 21/35 | 273.1 | 355 | 430 | 381 | 12 | 26
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 270 | 325 | 385 | 345 | 12 | 23
| 10K | 270 | 333 | 400 | 355 | 12 | 25
| 16K | 270 | 356 | 430 | 380 | 12 | 27
| 20K | 270 | 356 | 430 | 380 | 12 | 27
| 30K | 270 | 360 | 450 | 390 | 12 | 33
| 40K | 270 | 380 | 475 | 410 | 12 | 33
| 63K | 270 | 394 | 500 | 430 | 12 | 39
AWWA C207-01 | Class B | 276.352 | 338.1 | 406.4 | 361.95 | 12 | 25.4
| Class D | 276.352 | 338.1 | 406.4 | 361.95 | 12 | 25.4
| Class E | 276.352 | 338.1 | 406.4 | 361.95 | 12 | 25.4
| Class F | 276.352 | 360.4 | 444.5 | 387.35 | 16 | 28.575
DIN 86071 | PN6 | 282 | - | 375 | 335 | 12 | 18
| PN10 | 282 | - | 395 | 350 | 12 | 22
| PN16 | 282 | - | 405 | 355 | 12 | 26
| PN25 | 282 | - | 425 | 370 | 12 | 30
ISO7483 | PN2.5 | 273 | 317 | 375 | 335 | 12 | 18
| PN6 | 273 | 317 | 375 | 335 | 12 | 18
| PN10 | 273 | 328 | 395 | 350 | 12 | 22
| PN16 | 273 | 329 | 405 | 355 | 12 | 26
| PN20 | 273 | 338 | 405 | 362 | 12 | 26
| PN25 | 273 | 340 | 425 | 370 | 12 | 30
| PN40 | 273 | 352 | 450 | 385 | 12 | 33
| PN50 | 273 | 360.5 | - | - | - | -
| PN110 | 273 | 399 | - | - | - | -
| PN150 | 273 | 434 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 300mm
12" / 300mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 323.85 | 409.448 | 482.6 | 431.8 | 12 | 25.4
EN12560-1 | ASA150 | 323.85 | 409.448 | 482.6 | 431.8 | 12 | 25.4
Nominal Bore | ASA300 | 323.85 | 422.148 | 520.7 | 450.85 | 16 | 31.75
| ASA600 | 323.85 | 457.2 | 558.8 | 488.95 | 20 | 35.052
ANSI B16.21 & | ASA125 | 304.8 | 409.448 | 482.6 | 431.8 | 12 | 25.4
EN12560-1 | ASA150 | 304.8 | 409.448 | 482.6 | 431.8 | 12 | 25.4
True Bore | ASA300 | 304.8 | 422.148 | 520.7 | 450.85 | 16 | 31.75
| ASA600 | 304.8 | 457.2 | 558.8 | 488.95 | 20 | 35.052
BS3063 | BST A | 323.85 | 384.175 | 457.2 | 406.4 | 8 | 22.225
Nominal Bore | BST D | 323.85 | 384.175 | 457.2 | 406.4 | 12 | 22.225
| BST E | 323.85 | 380.4 | 457.2 | 406.4 | 12 | 26
| BST F | 323.85 | 412.15 | 488.95 | 438.15 | 16 | 26
| BST H | 323.85 | 412.15 | 488.95 | 438.15 | 16 | 26
| BST J | 323.85 | 408.15 | 488.95 | 438.15 | 16 | 30
| BST K | 323.85 | 399 | 488.95 | 432 | 16 | 33
| BST R | 323.85 | 424 | 510 | 457 | 16 | 33
BS3063 | BST A | 304.8 | 384.175 | 457.2 | 406.4 | 8 | 22.225
True Bore | BST D | 304.8 | 384.175 | 457.2 | 406.4 | 12 | 22.225
| BST E | 304.8 | 380.4 | 457.2 | 406.4 | 12 | 26
| BST F | 304.8 | 412.15 | 488.95 | 438.15 | 16 | 26
| BST H | 304.8 | 412.15 | 488.95 | 438.15 | 16 | 26
| BST J | 304.8 | 408.15 | 488.95 | 438.15 | 16 | 30
| BST K | 304.8 | 399 | 488.95 | 432 | 16 | 33
| BST R | 304.8 | 424 | 510 | 457 | 16 | 33
BS EN 1514-1 | PN2.5 | 325 | 373 | 440 | 395 | 12 | 22
& DIN2690 | PN6 | 325 | 373 | 440 | 395 | 12 | 22
| PN10 | 325 | 378 | 445 | 400 | 12 | 22
| PN16 | 325 | 385 | 460 | 410 | 12 | 26
| PN25 | 325 | 402 | 485 | 430 | 16 | 30
| PN40 | 325 | 418 | 515 | 450 | 16 | 33
AS4087 | Class 14/16 | 323.9 | 384 | 455 | 406 | 12 | 22
| Class 21/35 | 323.9 | 412 | 490 | 438 | 16 | 26
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 321 | 370 | 430 | 390 | 12 | 23
| 10K | 321 | 378 | 445 | 400 | 16 | 25
| 16K | 321 | 406 | 480 | 430 | 16 | 27
| 20K | 321 | 406 | 480 | 430 | 16 | 27
| 30K | 321 | 420 | 515 | 450 | 16 | 33
| 40K | 321 | 434 | 540 | 470 | 16 | 39
| 63K | 321 | 449 | 560 | 485 | 16 | 39
AWWA C207-01 | Class B | 327.152 | 408 | 482.6 | 431.8 | 12 | 25.4
| Class D | 327.152 | 408 | 482.6 | 431.8 | 12 | 25.4
| Class E | 327.152 | 408 | 482.6 | 431.8 | 12 | 25.4
| Class F | 327.152 | 420.7 | 520.7 | 450.85 | 16 | 31.75
DIN 86071 | PN6 | 332 | - | 440 | 395 | 12 | 22
| PN10 | 332 | - | 445 | 400 | 12 | 22
| PN16 | 332 | - | 460 | 410 | 12 | 26
| PN25 | 332 | - | 485 | 430 | 16 | 30
ISO7483 | PN2.5 | 324 | 373 | 440 | 395 | 12 | 22
| PN6 | 324 | 373 | 440 | 395 | 12 | 22
| PN10 | 324 | 378 | 445 | 400 | 12 | 22
| PN16 | 324 | 384 | 460 | 410 | 12 | 26
| PN20 | 324 | 408 | 485 | 432 | 12 | 26
| PN25 | 324 | 400 | 485 | 430 | 16 | 30
| PN40 | 324 | 417 | 515 | 450 | 16 | 33
| PN50 | 324 | 421 | - | - | - | -
| PN110 | 324 | 456 | - | - | - | -
| PN150 | 324 | 497.5 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 350mm
14" / 350mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 355.6 | 450.85 | 533.4 | 476.25 | 12 | 28.448
EN12560-1 | ASA150 | 355.6 | 450.85 | 533.4 | 476.25 | 12 | 28.448
Nominal Bore | ASA300 | 355.6 | 485.648 | 584.2 | 514.35 | 20 | 31.75
| ASA600 | 355.6 | 492.252 | 603.25 | 527.05 | 20 | 38.1
ANSI B16.21 & | ASA125 | 355.6 | 450.85 | 533.4 | 476.25 | 12 | 28.448
EN12560-1 | ASA150 | 355.6 | 450.85 | 533.4 | 476.25 | 12 | 28.448
True Bore | ASA300 | 355.6 | 485.648 | 584.2 | 514.35 | 20 | 31.75
| ASA600 | 355.6 | 492.252 | 603.25 | 527.05 | 20 | 38.1
BS3063 | BST A | 381 | 444.5 | 527.05 | 469.9 | 8 | 25.4
Nominal Bore | BST D | 381 | 444.5 | 527.05 | 469.9 | 12 | 25.4
| BST E | 381 | 444.5 | 527.05 | 469.9 | 12 | 25.4
| BST F | 381 | 466.725 | 552.45 | 495.3 | 16 | 28.575
| BST H | 381 | 466.725 | 552.45 | 495.3 | 16 | 28.575
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 355.6 | 444.5 | 527.05 | 469.9 | 8 | 25.4
True Bore | BST D | 355.6 | 444.5 | 527.05 | 469.9 | 12 | 25.4
| BST E | 355.6 | 444.5 | 527.05 | 469.9 | 12 | 25.4
| BST F | 355.6 | 466.725 | 552.45 | 495.3 | 16 | 28.575
| BST H | 355.6 | 466.725 | 552.45 | 495.3 | 16 | 28.575
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | 368 | 423 | 490 | 445 | 12 | 22
& DIN2690 | PN6 | 368 | 423 | 490 | 445 | 12 | 22
| PN10 | 368 | 438 | 505 | 460 | 16 | 22
| PN16 | 368 | 445 | 520 | 470 | 16 | 26
| PN25 | 368 | 458 | 555 | 490 | 16 | 33
| PN40 | 368 | 475 | 580 | 510 | 16 | 36
AS4087 | Class 14/16 | 381 | 444 | 525 | 470 | 12 | 26
| Class 21/35 | 381 | 465 | 550 | 495 | 16 | 30
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 359 | 413 | 480 | 435 | 12 | 25
| 10K | 359 | 423 | 490 | 445 | 16 | 25
| 16K | 359 | 450 | 540 | 480 | 16 | 33
| 20K | 359 | 450 | 540 | 480 | 16 | 33
| 30K | 359 | 465 | 560 | 495 | 16 | 33
| 40K | 359 | 479 | 585 | 515 | 16 | 39
| 63K | 359 | 488 | 615 | 530 | 16 | 46
AWWA C207-01 | Class B | 360.426 | 449.3 | 533.4 | 476.25 | 12 | 28.575
| Class D | 360.426 | 449.3 | 533.4 | 476.25 | 12 | 28.575
| Class E | 360.426 | 449.3 | 533.4 | 476.25 | 12 | 28.575
| Class F | 360.426 | 484.2 | 584.2 | 514.35 | 20 | 31.75
DIN 86071 | PN6 | 363 | - | 490 | 445 | 12 | 22
| PN10 | 363 | - | 505 | 460 | 16 | 22
| PN16 | 363 | - | 520 | 470 | 16 | 26
| PN25 | 363 | - | 555 | 490 | 16 | 33
ISO7483 | PN2.5 | 356 | 423 | 490 | 445 | 12 | 22
| PN6 | 356 | 423 | 490 | 445 | 12 | 22
| PN10 | 356 | 438 | 505 | 460 | 16 | 22
| PN16 | 356 | 444 | 520 | 470 | 16 | 26
| PN20 | 356 | 449 | 535 | 476 | 12 | 29.5
| PN25 | 356 | 457 | 555 | 490 | 16 | 33
| PN40 | 356 | 474 | 580 | 510 | 16 | 36
| PN50 | 356 | 484.5 | - | - | - | -
| PN110 | 356 | 491 | - | - | - | -
| PN150 | 356 | 520 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 375mm
15" / 375mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | - | - | - | - | - | -
EN12560-1 | ASA150 | - | - | - | - | - | -
Nominal Bore | ASA300 | - | - | - | - | - | -
| ASA600 | - | - | - | - | - | -
ANSI B16.21 & | ASA125 | - | - | - | - | - | -
EN12560-1 | ASA150 | - | - | - | - | - | -
True Bore | ASA300 | - | - | - | - | - | -
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
Nominal Bore | BST D | 406.4 | 469.9 | 552.45 | 495.3 | 12 | 25.4
| BST E | 406.4 | 469.9 | 552.45 | 495.3 | 12 | 25.4
| BST F | 406.4 | 492.125 | 577.3 | 520.7 | 16 | 28.575
| BST H | 406.4 | 492.125 | 577.3 | 520.7 | 16 | 28.575
| BST J | 406.4 | 488.9 | 577.3 | 520.7 | 16 | 31.8
| BST K | 396.9 | 517.4 | 603.3 | 552.5 | 20 | 35.1
| BST R | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
True Bore | BST D | 381 | 469.9 | 552.45 | 495.3 | 12 | 25.4
| BST E | 381 | 469.9 | 552.45 | 495.3 | 12 | 25.4
| BST F | 381 | 492.125 | 577.3 | 520.7 | 16 | 28.575
| BST H | 381 | 492.125 | 577.3 | 520.7 | 16 | 28.575
| BST J | 381 | 488.9 | 577.3 | 520.7 | 16 | 31.8
| BST K | 381 | 517.4 | 603.3 | 552.5 | 20 | 35.1
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | 406.4 | 469 | 550 | 495 | 12 | 26
| Class 21/35 | 406.4 | 491 | 580 | 521 | 16 | 30
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | - | - | - | - | - | -
| 10K | - | - | - | - | - | -
| 16K | - | - | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | - | - | - | - | - | -
| PN110 | - | - | - | - | - | -
| PN150 | - | - | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 400mm
16" / 400mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 406.4 | 514.35 | 596.9 | 539.75 | 16 | 28.448
EN12560-1 | ASA150 | 406.4 | 514.35 | 596.9 | 539.75 | 16 | 28.448
Nominal Bore | ASA300 | 406.4 | 539.75 | 647.7 | 571.5 | 20 | 35.052
| ASA600 | 406.4 | 565.15 | 685.8 | 603.25 | 20 | 41.148
ANSI B16.21 & | ASA125 | 406.4 | 514.35 | 596.9 | 539.75 | 16 | 28.448
EN12560-1 | ASA150 | 406.4 | 514.35 | 596.9 | 539.75 | 16 | 28.448
True Bore | ASA300 | 406.4 | 539.75 | 647.7 | 571.5 | 20 | 35.052
| ASA600 | 406.4 | 565.15 | 685.8 | 603.25 | 20 | 41.148
BS3063 | BST A | 431.8 | 495.3 | 577.85 | 520.7 | 12 | 25.4
Nominal Bore | BST D | 431.8 | 495.3 | 577.85 | 520.7 | 12 | 25.4
| BST E | 431.8 | 495.3 | 577.85 | 520.7 | 12 | 25.4
| BST F | 431.8 | 522.45 | 609.6 | 552.45 | 20 | 30
| BST H | 431.8 | 522.45 | 609.6 | 552.45 | 20 | 30
| BST J | 431.8 | 519.45 | 609.6 | 552.45 | 20 | 33
| BST K | 431.8 | 529 | 630 | 565 | 20 | 36
| BST R | 431.8 | 548 | 640 | 584 | 20 | 36
BS3063 | BST A | 406.4 | 495.3 | 577.85 | 520.7 | 12 | 25.4
True Bore | BST D | 406.4 | 495.3 | 577.85 | 520.7 | 12 | 25.4
| BST E | 406.4 | 495.3 | 577.85 | 520.7 | 12 | 25.4
| BST F | 406.4 | 522.45 | 609.6 | 552.45 | 20 | 30
| BST H | 406.4 | 522.45 | 609.6 | 552.45 | 20 | 30
| BST J | 406.4 | 519.45 | 609.6 | 552.45 | 20 | 33
| BST K | 406.4 | 529 | 630 | 565 | 20 | 36
| BST R | 406.4 | 548 | 640 | 584 | 20 | 36
BS EN 1514-1 | PN2.5 | 420 | 473 | 540 | 495 | 16 | 22
& DIN2690 | PN6 | 420 | 473 | 540 | 495 | 16 | 22
| PN10 | 420 | 490 | 565 | 515 | 16 | 26
| PN16 | 420 | 497 | 580 | 525 | 16 | 30
| PN25 | 420 | 515 | 620 | 550 | 16 | 36
| PN40 | 420 | 547 | 660 | 585 | 16 | 39
AS4087 | Class 14/16 | 431.8 | 495 | 580 | 521 | 12 | 26
| Class 21/35 | 431.8 | 522 | 610 | 552 | 20 | 30
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | 410 | 473 | 540 | 495 | 16 | 25
| 10K | 410 | 486 | 560 | 510 | 16 | 27
| 16K | 410 | 510 | 605 | 540 | 16 | 33
| 20K | 410 | 510 | 605 | 540 | 16 | 33
| 30K | 410 | 524 | 630 | 560 | 16 | 39
| 40K | 410 | 534 | 645 | 570 | 16 | 39
| 63K | 410 | 548 | 680 | 590 | 16 | 46
AWWA C207-01 | Class B | 411.226 | 512.8 | 596.9 | 539.75 | 16 | 28.575
| Class D | 411.226 | 512.8 | 596.9 | 539.75 | 16 | 28.575
| Class E | 411.226 | 512.8 | 596.9 | 539.75 | 16 | 28.575
| Class F | 411.226 | 538.2 | 647.7 | 571.5 | 20 | 34.925
DIN 86071 | PN6 | 415 | - | 540 | 495 | 16 | 22
| PN10 | 415 | - | 565 | 515 | 16 | 26
| PN16 | 415 | - | 580 | 525 | 16 | 30
| PN25 | 415 | - | 620 | 550 | 16 | 36
ISO7483 | PN2.5 | 407 | 473 | 540 | 495 | 16 | 22
| PN6 | 407 | 473 | 540 | 495 | 16 | 22
| PN10 | 407 | 489 | 565 | 515 | 16 | 26
| PN16 | 407 | 495 | 580 | 525 | 16 | 30
| PN20 | 407 | 513 | 600 | 540 | 16 | 29.5
| PN25 | 407 | 514 | 620 | 550 | 16 | 36
| PN40 | 407 | 546 | 660 | 585 | 16 | 39
| PN50 | 407 | 538.5 | - | - | - | -
| PN110 | 407 | 564 | - | - | - | -
| PN150 | 407 | 574 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 450mm
18" / 450mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 457.2 | 549.148 | 635 | 577.85 | 16 | 31.75
EN12560-1 | ASA150 | 457.2 | 549.148 | 635 | 577.85 | 16 | 31.75
Nominal Bore | ASA300 | 457.2 | 596.9 | 711.2 | 628.65 | 24 | 35.052
| ASA600 | 457.2 | 612.648 | 742.95 | 654.05 | 20 | 44.45
ANSI B16.21 & | ASA125 | 457.2 | 549.148 | 635 | 577.85 | 16 | 31.75
EN12560-1 | ASA150 | 457.2 | 549.148 | 635 | 577.85 | 16 | 31.75
True Bore | ASA300 | 457.2 | 596.9 | 711.2 | 628.65 | 24 | 35.052
| ASA600 | 457.2 | 612.648 | 742.95 | 654.05 | 20 | 44.45
BS3063 | BST A | 482.6 | 558.8 | 641.35 | 584.2 | 12 | 25.4
Nominal Bore | BST D | 482.6 | 558.8 | 641.35 | 584.2 | 12 | 25.4
| BST E | 482.6 | 558.8 | 641.35 | 584.2 | 16 | 25.4
| BST F | 482.6 | 576.6 | 673.1 | 609.6 | 20 | 33
| BST H | 482.6 | 576.6 | 673.1 | 609.6 | 20 | 33
| BST J | 482.6 | 573.6 | 673.1 | 609.6 | 20 | 36
| BST K | 482.6 | 615 | 720 | 654 | 20 | 39
| BST R | 482.6 | 634 | 735 | 673 | 20 | 39
BS3063 | BST A | 457.2 | 558.8 | 641.35 | 584.2 | 12 | 25.4
True Bore | BST D | 457.2 | 558.8 | 641.35 | 584.2 | 12 | 25.4
| BST E | 457.2 | 558.8 | 641.35 | 584.2 | 16 | 25.4
| BST F | 457.2 | 576.6 | 673.1 | 609.6 | 20 | 33
| BST H | 457.2 | 576.6 | 673.1 | 609.6 | 20 | 33
| BST J | 457.2 | 573.6 | 673.1 | 609.6 | 20 | 36
| BST K | 457.2 | 615 | 720 | 654 | 20 | 39
| BST R | 457.2 | 634 | 735 | 673 | 20 | 39
BS EN 1514-1 | PN2.5 | 470 | 528 | 595 | 550 | 16 | 22
& DIN2690 | PN6 | 470 | 528 | 595 | 550 | 16 | 22
| PN10 | 470 | 540 | 615 | 565 | 20 | 26
| PN16 | 470 | 557 | 640 | 585 | 20 | 30
| PN25 | 470 | 565 | - | - | - | -
| PN40 | 470 | 572 | 685 | 610 | 20 | 39
AS4087 | Class 14/16 | 482.6 | 558 | 640 | 584 | 12 | 26
| Class 21/35 | 482.6 | 577 | 675 | 610 | 20 | 33
JIS B2202 | 2K | 460 | 535 | 605 | 555 | 16 | 23
| 5K | 460 | 533 | 605 | 555 | 16 | 25
| 10K | 460 | 541 | 620 | 565 | 20 | 27
| 16K | 460 | 575 | 675 | 605 | 20 | 33
| 20K | 460 | 575 | 675 | 605 | 20 | 33
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | 462.026 | 547.7 | 635 | 577.85 | 16 | 31.75
| Class D | 462.026 | 547.7 | 635 | 577.85 | 16 | 31.75
| Class E | 462.026 | 547.7 | 635 | 577.85 | 16 | 31.75
| Class F | 462.026 | 595.3 | 711.2 | 628.65 | 24 | 34.925
DIN 86071 | PN6 | 467 | - | 595 | 550 | 16 | 22
| PN10 | 467 | - | 615 | 565 | 20 | 26
| PN16 | 467 | - | 640 | 585 | 20 | 30
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | 458 | 528 | 595 | 550 | 16 | 22
| PN6 | 458 | 528 | 595 | 550 | 16 | 22
| PN10 | 458 | 539 | 615 | 565 | 20 | 26
| PN16 | 458 | 555 | 640 | 585 | 20 | 30
| PN20 | 458 | 548 | 635 | 578 | 16 | 32.5
| PN25 | 458 | 564 | 670 | 600 | 20 | 36
| PN40 | 458 | 571 | 685 | 610 | 20 | 39
| PN50 | 458 | 595.5 | - | - | - | -
| PN110 | 458 | 612 | - | - | - | -
| PN150 | 458 | 638 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 500mm
20" / 500mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 508 | 606.552 | 698.5 | 635 | 20 | 31.75
EN12560-1 | ASA150 | 508 | 606.552 | 698.5 | 635 | 20 | 31.75
Nominal Bore | ASA300 | 508 | 654.05 | 774.7 | 685.8 | 24 | 35.052
| ASA600 | 508 | 682.752 | 812.8 | 723.9 | 24 | 44.45
ANSI B16.21 & | ASA125 | 508 | 606.552 | 698.5 | 635 | 20 | 31.75
EN12560-1 | ASA150 | 508 | 606.552 | 698.5 | 635 | 20 | 31.75
True Bore | ASA300 | 508 | 654.05 | 774.7 | 685.8 | 24 | 35.052
| ASA600 | 508 | 682.752 | 812.8 | 723.9 | 24 | 44.45
BS3063 | BST A | 533.4 | 615.95 | 704.85 | 641.35 | 12 | 25.4
Nominal Bore | BST D | 533.4 | 615.95 | 704.85 | 641.35 | 16 | 25.4
| BST E | 533.4 | 615.95 | 704.85 | 641.35 | 16 | 25.4
| BST F | 533.4 | 640.1 | 736.6 | 673.1 | 24 | 33
| BST H | 533.4 | 640.1 | 736.6 | 673.1 | 24 | 33
| BST J | 533.4 | 637.1 | 736.6 | 673.1 | 24 | 36
| BST K | 533.4 | 669 | 785 | 711 | 20 | 42
| BST R | 533.4 | 688 | 805 | 730 | 20 | 42
BS3063 | BST A | 508 | 615.95 | 704.85 | 641.35 | 12 | 25.4
True Bore | BST D | 508 | 615.95 | 704.85 | 641.35 | 16 | 25.4
| BST E | 508 | 615.95 | 704.85 | 641.35 | 16 | 25.4
| BST F | 508 | 640.1 | 736.6 | 673.1 | 24 | 33
| BST H | 508 | 640.1 | 736.6 | 673.1 | 24 | 33
| BST J | 508 | 637.1 | 736.6 | 673.1 | 24 | 36
| BST K | 508 | 669 | 785 | 711 | 20 | 42
| BST R | 508 | 688 | 805 | 730 | 20 | 42
BS EN 1514-1 | PN2.5 | 520 | 578 | 645 | 600 | 20 | 22
& DIN2690 | PN6 | 520 | 578 | 645 | 600 | 20 | 22
| PN10 | 520 | 595 | 670 | 620 | 20 | 26
| PN16 | 520 | 618 | 715 | 650 | 20 | 33
| PN25 | 520 | 625 | 730 | 660 | 20 | 36
| PN40 | 520 | 628 | 755 | 670 | 20 | 42
AS4087 | Class 14/16 | 533.4 | 615 | 705 | 641 | 16 | 26
| Class 21/35 | 533.4 | 640 | 735 | 673 | 24 | 33
JIS B2202 | 2K | 513 | 585 | 655 | 605 | 20 | 23
| 5K | 513 | 583 | 655 | 605 | 20 | 25
| 10K | 513 | 596 | 675 | 620 | 20 | 27
| 16K | 513 | 630 | 730 | 660 | 20 | 33
| 20K | 513 | 630 | 730 | 660 | 20 | 33
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | 512.826 | 604.8 | 698.5 | 635 | 20 | 31.75
| Class D | 512.826 | 604.8 | 698.5 | 635 | 20 | 31.75
| Class E | 512.826 | 604.8 | 698.5 | 635 | 20 | 31.75
| Class F | 512.826 | 652.5 | 774.7 | 685.8 | 24 | 34.925
DIN 86071 | PN6 | 520 | - | 645 | 600 | 20 | 22
| PN10 | 520 | - | 670 | 620 | 20 | 26
| PN16 | 520 | - | 715 | 650 | 20 | 33
| PN25 | 520 | - | 730 | 660 | 20 | 36
ISO7483 | PN2.5 | 508 | 578 | 645 | 600 | 20 | 22
| PN6 | 508 | 578 | 645 | 600 | 20 | 22
| PN10 | 508 | 594 | 670 | 620 | 20 | 26
| PN16 | 508 | 617 | 715 | 650 | 20 | 33
| PN20 | 508 | 605 | 700 | 635 | 20 | 32.5
| PN25 | 508 | 624 | 730 | 660 | 20 | 36
| PN40 | 508 | 628 | 755 | 670 | 20 | 42
| PN50 | 508 | 653 | - | - | - | -
| PN110 | 508 | 682 | - | - | - | -
| PN150 | 508 | 697.5 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 550mm
22" / 550mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | - | - | - | - | - | -
EN12560-1 | ASA150 | 559 | 660 | 749.3 | 692.2 | 20 | 34.9
Nominal Bore | ASA300 | 559 | 705 | - | - | - | -
| ASA600 | 559 | 733 | - | - | - | -
ANSI B16.21 & | ASA125 | - | - | - | - | - | -
EN12560-1 | ASA150 | - | - | - | - | - | -
True Bore | ASA300 | - | - | - | - | - | -
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | 584.2 | 669.925 | 762 | 698.5 | 12 | 28.575
Nominal Bore | BST D | 584.2 | 669.925 | 762 | 698.5 | 16 | 28.575
| BST E | 584.2 | 669.925 | 762 | 698.5 | 16 | 28.575
| BST F | 584.2 | 690.9 | 787.4 | 723.9 | 24 | 33
| BST H | 584.2 | 690.9 | 787.4 | 723.9 | 24 | 33
| BST J | 584.2 | 687.9 | 787.4 | 723.9 | 24 | 36
| BST K | 584.2 | 726 | 870 | 781 | 20 | 55
| BST R | 584.2 | 751 | 895 | 806 | 20 | 55
BS3063 | BST A | 558.8 | 669.925 | 762 | 698.5 | 12 | 28.575
True Bore | BST D | 558.8 | 669.925 | 762 | 698.5 | 16 | 28.575
| BST E | 558.8 | 669.925 | 762 | 698.5 | 16 | 28.575
| BST F | 558.8 | 690.9 | 787.4 | 723.9 | 24 | 33
| BST H | 558.8 | 690.9 | 787.4 | 723.9 | 24 | 33
| BST J | 558.8 | 687.9 | 787.4 | 723.9 | 24 | 36
| BST K | 558.8 | 726 | 870 | 781 | 20 | 55
| BST R | 558.8 | 751 | 895 | 806 | 20 | 55
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | 564 | 643 | 720 | 665 | 20 | 25
| 5K | 564 | 641 | 720 | 665 | 20 | 27
| 10K | 564 | 650 | 745 | 680 | 20 | 33
| 16K | 564 | 684 | 795 | 720 | 20 | 39
| 20K | 564 | 684 | 795 | 720 | 20 | 39
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
|  | - | - | - | - | - | -
AWWA C207-01 | Class B | 563.626 | 658.8 | 749.3 | 692.15 | 20 | 34.925
| Class D | 563.626 | 658.8 | 749.3 | 692.15 | 20 | 34.925
| Class E | 563.626 | 658.8 | 749.3 | 692.15 | 20 | 34.925
| Class F | 563.626 | 709.6 | 838.2 | 742.95 | 24 | 34.925
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | - | - | - | - | - | -
| PN110 | - | - | - | - | - | -
| PN150 | - | - | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 600mm
24" / 600mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 & | ASA125 | 609.6 | 717.55 | 812.8 | 749.3 | 20 | 35.052
EN12560-1 | ASA150 | 609.6 | 717.55 | 812.8 | 749.3 | 20 | 35.052
Nominal Bore | ASA300 | 609.6 | 774.7 | 914.4 | 812.8 | 24 | 41.148
| ASA600 | 609.6 | 790.448 | 939.8 | 838.2 | 24 | 50.8
ANSI B16.21 & | ASA125 | 609.6 | 717.55 | 812.8 | 749.3 | 20 | 35.052
EN12560-1 | ASA150 | 609.6 | 717.55 | 812.8 | 749.3 | 20 | 35.052
True Bore | ASA300 | 609.6 | 774.7 | 914.4 | 812.8 | 24 | 41.148
| ASA600 | 609.6 | 790.448 | 939.8 | 838.2 | 24 | 50.8
BS3063 | BST A | 635 | 727.075 | 825.5 | 755.65 | 12 | 28.575
Nominal Bore | BST D | 635 | 727.075 | 825.5 | 755.65 | 16 | 28.575
| BST E | 635 | 722.65 | 825.5 | 755.65 | 16 | 33
| BST F | 635 | 745.05 | 850.9 | 781.05 | 24 | 36
| BST H | 635 | 745.05 | 850.9 | 781.05 | 24 | 36
| BST J | 635 | 742.05 | 850.9 | 781.05 | 24 | 39
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 609.6 | 727.075 | 825.5 | 755.65 | 12 | 28.575
True Bore | BST D | 609.6 | 727.075 | 825.5 | 755.65 | 16 | 28.575
| BST E | 609.6 | 722.65 | 825.5 | 755.65 | 16 | 33
| BST F | 609.6 | 745.05 | 850.9 | 781.05 | 24 | 36
| BST H | 609.6 | 745.05 | 850.9 | 781.05 | 24 | 36
| BST J | 609.6 | 742.05 | 850.9 | 781.05 | 24 | 39
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | 620 | 680 | 755 | 705 | 20 | 26
& DIN2690 | PN6 | 620 | 680 | 755 | 705 | 20 | 26
| PN10 | 620 | 695 | 780 | 725 | 20 | 30
| PN16 | 620 | 735 | 840 | 770 | 20 | 36
| PN25 | 620 | 730 | 845 | 770 | 20 | 39
| PN40 | 620 | 745 | 890 | 795 | 20 | 48
AS4087 | Class 14/16 | 635 | 726 | 825 | 756 | 16 | 30
| Class 21/35 | 635 | 745 | 850 | 781 | 24 | 36
JIS B2202 | 2K | 615 | 693 | 770 | 715 | 20 | 25
| 5K | 615 | 691 | 770 | 715 | 20 | 27
| 10K | 615 | 700 | 795 | 730 | 24 | 33
| 16K | 615 | 734 | 845 | 770 | 24 | 39
| 20K | 615 | 734 | 845 | 770 | 24 | 39
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | 614.426 | 716 | 812.8 | 749.3 | 20 | 34.925
| Class D | 614.426 | 716 | 812.8 | 749.3 | 20 | 34.925
| Class E | 614.426 | 716 | 812.8 | 749.3 | 20 | 34.925
| Class F | 614.426 | 773.1 | 914.4 | 812.8 | 24 | 41.275
DIN 86071 | PN6 | 620 | - | 755 | 705 | 20 | 26
| PN10 | 620 | - | 780 | 725 | 20 | 30
| PN16 | 620 | - | 840 | 770 | 20 | 36
| PN25 | 620 | - | 845 | 770 | 20 | 39
ISO7483 | PN2.5 | 610 | 679 | 755 | 705 | 20 | 26
| PN6 | 610 | 679 | 755 | 705 | 20 | 26
| PN10 | 610 | 695 | 780 | 725 | 20 | 30
| PN16 | 610 | 734 | 840 | 770 | 20 | 36
| PN20 | 610 | 716.5 | 815 | 749.5 | 20 | 35.5
| PN25 | 610 | 731 | 845 | 770 | 20 | 39
| PN40 | 610 | 747 | 890 | 795 | 20 | 48
| PN50 | 610 | 774 | - | - | - | -
| PN110 | 610 | 790 | - | - | - | -
| PN150 | 610 | 837.5 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 650mm
26" / 650mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | 660 | 775 | 870 | 806.5 | 24 | 35.1
| ASA300 | 660 | 835 | 971.6 | 876.3 | 28 | 44.5
| ASA600 | 660 | 867 | 1016 | 914.4 | 28 | 50.8
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 660 | 725 | 785.9 | 744.5 | 36 | 22.4
| ASA300 | 660 | 772 | 866.6 | 803.1 | 32 | 35.1
| ASA600 | 660 | 765 | 889 | 806.5 | 28 | 44.5
BS3063 | BST A | 685.8 | 751 | 845 | 781 | 16 | 30
Nominal Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 660.4 | 751 | 845 | 781 | 16 | 30
True Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | 667 | 748 | 825 | 770 | 24 | 25
| 5K | 667 | 746 | 825 | 770 | 24 | 27
| 10K | 667 | 750 | 845 | 780 | 24 | 33
| 16K | 667 | 784 | - | - | - | -
| 20K | 667 | 805 | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | 665.2 | 773.1 | 870 | 806.5 | 24 | 34.9
| Class D | 665.2 | 773.1 | 870 | 806.5 | 24 | 34.9
| Class E | 665.2 | 773.1 | 870 | 806.5 | 24 | 34.9
| Class F | 666.8 | 830.3 | 971.6 | 876.3 | 28 | 47.6
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | 660 | 773 | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | 660 | 834 | - | - | - | -
| PN110 | 660 | 866 | - | - | - | -
| PN150 | 660 | 880 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 700mm
28" / 700mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | 711 | 832 | 927.1 | 863.6 | 28 | 35.1
| ASA300 | 711 | 899 | 1035.1 | 939.8 | 28 | 44.5
| ASA600 | 711 | 914 | 1073.2 | 965.2 | 28 | 53.8
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 711 | 779 | 836.7 | 795.3 | 40 | 22.4
| ASA300 | 711 | 826 | 920.8 | 857.3 | 36 | 35.1
| ASA600 | 711 | 819 | 952.5 | 863.6 | 28 | 47.8
BS3063 | BST A | 736.6 | 776 | 870 | 806 | 16 | 30
Nominal Bore | BST D | 736.6 | 815 | 910 | 845 | 20 | 30
| BST E | 736.6 | 812 | 910 | 845 | 20 | 33
| BST F | 736.6 | 821 | 935 | 857 | 24 | 36
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 711.2 | 776 | 870 | 806 | 16 | 30
True Bore | BST D | 711.2 | 815 | 910 | 845 | 20 | 30
| BST E | 711.2 | 812 | 910 | 845 | 20 | 33
| BST F | 711.2 | 821 | 935 | 857 | 24 | 36
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | 720 | 785 | 860 | 810 | 24 | 26
& DIN2690 | PN6 | 720 | 785 | 860 | 810 | 24 | 26
| PN10 | 720 | 810 | 895 | 840 | 24 | 30
| PN16 | 720 | 805 | 910 | 840 | 24 | 36
| PN25 | 720 | 830 | 960 | 875 | 24 | 42
| PN40 | 720 | 850 | 995 | 900 | 24 | 48
AS4087 | Class 14/16 | 736.6 | 815 | 910 | 845 | 20 | 30
| Class 21/35 | 736.6 | 821 | 935 | 857 | 24 | 36
JIS B2202 | 2K | 718 | 798 | 875 | 820 | 24 | 25
| 5K | 718 | 796 | 875 | 820 | 24 | 27
| 10K | 718 | 810 | 905 | 840 | 24 | 33
| 16K | 718 | 836 | - | - | - | -
| 20K | 718 | 855 | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | 716 | 830.3 | 927.1 | 863.6 | 28 | 34.9
| Class D | 716 | 830.3 | 927.1 | 863.6 | 28 | 34.9
| Class E | 716 | 830.3 | 927.1 | 863.6 | 28 | 34.9
| Class F | 717.6 | 893.8 | 1035.1 | 939.8 | 28 | 47.6
DIN 86071 | PN6 | 723 | - | 860 | 810 | 24 | 26
| PN10 | 723 | - | 895 | 840 | 24 | 30
| PN16 | 723 | - | 910 | 840 | 24 | 36
| PN25 | 723 | - | 960 | 875 | 24 | 42
ISO7483 | PN2.5 | 712 | 784 | - | - | - | -
| PN6 | 712 | 784 | - | - | - | -
| PN10 | 712 | 810 | 895 | 840 | 24 | 30
| PN16 | 712 | 804 | 910 | 840 | 24 | 36
| PN20 | 711 | 830 | - | - | - | -
| PN25 | 712 | 833 | 960 | 875 | 24 | 42
| PN40 | - | - | - | - | - | -
| PN50 | 711 | 898 | - | - | - | -
| PN110 | 711 | 913 | - | - | - | -
| PN150 | 711 | 946 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 750mm
30" / 750mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | 762 | 883 | 984 | 914.4 | 28 | 34.9
Series A | ASA150 | 762 | 883 | 984.3 | 914.4 | 28 | 35.1
| ASA300 | 762 | 953 | 1092.2 | 997 | 28 | 47.8
| ASA600 | 762 | 972 | 1130.3 | 1022.4 | 28 | 53.8
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 762 | 827 | 887.5 | 846.1 | 44 | 22.4
| ASA300 | 762 | 886 | 990.6 | 920.8 | 36 | 38.1
| ASA600 | 762 | 879 | 1022.4 | 927.1 | 28 | 50.8
BS3063 | BST A | 787.4 | 853 | 945 | 883 | 20 | 30
Nominal Bore | BST D | 787.4 | 894 | 995 | 927 | 20 | 33
| BST E | 787.4 | 891 | 995 | 927 | 20 | 36
| BST F | 787.4 | 904 | 1015 | 940 | 28 | 36
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 762 | 853 | 945 | 883 | 20 | 30
True Bore | BST D | 762 | 894 | 995 | 927 | 20 | 33
| BST E | 762 | 891 | 995 | 927 | 20 | 36
| BST F | 762 | 904 | 1015 | 940 | 28 | 36
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | 787.4 | 894 | 995 | 927 | 20 | 33
| Class 21/35 | 787.4 | 904 | 1015 | 940 | 28 | 36
JIS B2202 | 2K | 770 | 856 | 945 | 880 | 24 | 27
| 5K | 770 | 850 | 945 | 880 | 24 | 33
| 10K | 770 | 870 | 970 | 900 | 24 | 33
| 16K | 770 | 896 | - | - | - | -
| 20K | 770 | 918 | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | 766.8 | 881.1 | 984.3 | 914.4 | 28 | 34.9
| Class D | 766.8 | 881.1 | 984.3 | 914.4 | 28 | 34.9
| Class E | 766.8 | 881.1 | 984.3 | 914.4 | 28 | 34.9
| Class F | 768.4 | 950.9 | 1092.2 | 997 | 28 | 47.6
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | 762 | 881 | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | 762 | 952 | - | - | - | -
| PN110 | 762 | 970 | - | - | - | -
| PN150 | 762 | 1040 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 800mm
32" / 800mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | 813 | 940 | 1060.5 | 977.9 | 28 | 41.1
| ASA300 | 813 | 1006 | 1149.4 | 1054.1 | 28 | 50.8
| ASA600 | 813 | 1022 | 1193.8 | 1079.5 | 28 | 60.5
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 813 | 881 | 941.3 | 900.2 | 48 | 22.4
| ASA300 | 813 | 940 | 1054.1 | 977.9 | 32 | 41.1
| ASA600 | 813 | 933 | 1085.9 | 984.3 | 28 | 53.8
BS3063 | BST A | 838.2 | 910 | 1005 | 940 | 20 | 30
Nominal Bore | BST D | 838.2 | 948 | 1060 | 984 | 20 | 36
| BST E | 838.2 | 948 | 1060 | 984 | 20 | 36
| BST F | 838.2 | 948 | 1060 | 984 | 28 | 36
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 812.8 | 910 | 1005 | 940 | 20 | 30
True Bore | BST D | 812.8 | 948 | 1060 | 984 | 20 | 36
| BST E | 812.8 | 948 | 1060 | 984 | 20 | 36
| BST F | 812.8 | 948 | 1060 | 984 | 28 | 36
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | 820 | 890 | 975 | 920 | 24 | 30
& DIN2690 | PN6 | 820 | 890 | 975 | 920 | 24 | 30
| PN10 | 820 | 915 | 1015 | 950 | 24 | 33
| PN16 | 820 | 910 | 1025 | 950 | 24 | 39
| PN25 | 820 | 940 | 1085 | 990 | 24 | 48
| PN40 | 820 | 970 | 1140 | 1030 | 24 | 56
AS4087 | Class 14/16 | 838.2 | 948 | 1060 | 984 | 20 | 36
| Class 21/35 | 838.2 | 948 | 1060 | 984 | 28 | 36
JIS B2202 | 2K | 820 | 906 | 995 | 930 | 24 | 27
| 5K | 820 | 900 | 995 | 930 | 24 | 33
| 10K | 820 | 920 | 1020 | 950 | 28 | 33
| 16K | 820 | 945 | - | - | - | -
| 20K | 820 | 978 | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | 817.6 | 938.2 | 1060.5 | 977.9 | 28 | 41.3
| Class D | 817.6 | 938.2 | 1060.5 | 977.9 | 28 | 41.3
| Class E | 817.6 | 938.2 | 1060.5 | 977.9 | 28 | 41.3
| Class F | 819.2 | 1008.1 | 1149.4 | 1054.1 | 28 | 47.6
DIN 86071 | PN6 | 825 | - | 975 | 920 | 24 | 30
| PN10 | 825 | - | 1015 | 950 | 24 | 33
| PN16 | 825 | - | 1025 | 950 | 24 | 39
| PN25 | 825 | - | 1085 | 990 | 24 | 48
ISO7483 | PN2.5 | 813 | 890 | - | - | - | -
| PN6 | 813 | 890 | - | - | - | -
| PN10 | 813 | 917 | 1015 | 950 | 24 | 33
| PN16 | 813 | 911 | 1025 | 950 | 24 | 39
| PN20 | 813 | 939 | - | - | - | -
| PN25 | 813 | 942 | 1085 | 990 | 24 | 48
| PN40 | - | - | - | - | - | -
| PN50 | 813 | 1006 | - | - | - | -
| PN110 | 813 | 1024 | - | - | - | -
| PN150 | 813 | 1076 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 850mm
34" / 850mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | 864 | 991 | 1111.3 | 1028.7 | 32 | 41.1
| ASA300 | 864 | 1057 | 1206.5 | 1104.9 | 28 | 50.8
| ASA600 | 864 | 1073 | 1244.6 | 1130.3 | 28 | 60.5
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 864 | 935 | 1004.8 | 957.3 | 40 | 25.4
| ASA300 | 864 | 994 | 1107.9 | 1031.7 | 36 | 41.1
| ASA600 | 864 | 997 | 1162.1 | 1054.1 | 24 | 60.5
BS3063 | BST A | 889 | 935 | 1030 | 965 | 20 | 30
Nominal Bore | BST D | 889 | 980 | 1090 | 1016 | 20 | 36
| BST E | 889 | 980 | 1090 | 1016 | 20 | 36
| BST F | 889 | 980 | 1090 | 1016 | 32 | 36
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 863.6 | 935 | 1030 | 965 | 20 | 30
True Bore | BST D | 863.6 | 980 | 1090 | 1016 | 20 | 36
| BST E | 863.6 | 980 | 1090 | 1016 | 20 | 36
| BST F | 863.6 | 980 | 1090 | 1016 | 32 | 36
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | 872 | 956 | 1045 | 980 | 24 | 27
| 5K | 872 | 950 | 1045 | 980 | 24 | 33
| 10K | 872 | 970 | 1070 | 1000 | 28 | 33
| 16K | 872 | 995 | - | - | - | -
| 20K | 872 | 1038 | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | 868.4 | 989 | 1111.3 | 1028.7 | 32 | 41.3
| Class D | 868.4 | 989 | 1111.3 | 1028.7 | 32 | 41.3
| Class E | 868.4 | 989 | 1111.3 | 1028.7 | 32 | 41.3
| Class F | 870 | 1058.9 | 1206.5 | 1104.9 | 28 | 47.6
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | 864 | 990 | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | 864 | 1057 | - | - | - | -
| PN110 | 864 | 1074 | - | - | - | -
| PN150 | 864 | 1136 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 900mm
36" / 900mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | 914 | 1048 | 1168 | 1085.9 | 32 | 41.3
Series A | ASA150 | 914 | 1048 | 1168.4 | 1085.9 | 32 | 41.1
| ASA300 | 914 | 1118 | 1270 | 1168.4 | 32 | 53.8
| ASA600 | 914 | 1130 | 1314.5 | 1193.8 | 28 | 66.5
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 914 | 987 | 1057.1 | 1009.7 | 44 | 25.4
| ASA300 | 914 | 1048 | 1171.4 | 1089.2 | 32 | 44.5
| ASA600 | 914 | 1048 | 1212.9 | 1104.9 | 28 | 60.5
BS3063 | BST A | 939.8 | 1011 | 1105 | 1041 | 24 | 30
Nominal Bore | BST D | 939.8 | 1056 | 1175 | 1092 | 24 | 36
| BST E | 939.8 | 1056 | 1175 | 1092 | 24 | 36
| BST F | 939.8 | 1066 | 1185 | 1105 | 32 | 39
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 914.4 | 1011 | 1105 | 1041 | 24 | 30
True Bore | BST D | 914.4 | 1056 | 1175 | 1092 | 24 | 36
| BST E | 914.4 | 1056 | 1175 | 1092 | 24 | 36
| BST F | 914.4 | 1066 | 1185 | 1105 | 32 | 39
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | 920 | 990 | 1072 | 1020 | 24 | 30
& DIN2690 | PN6 | 920 | 990 | 1075 | 1020 | 24 | 30
| PN10 | 920 | 1015 | 1115 | 1050 | 28 | 33
| PN16 | 920 | 1010 | 1125 | 1050 | 28 | 39
| PN25 | 920 | 1040 | 1185 | 1090 | 28 | 48
| PN40 | 920 | 1080 | 1250 | 1140 | 28 | 56
AS4087 | Class 14/16 | 939.8 | 1056 | 1175 | 1092 | 24 | 36
| Class 21/35 | 939.8 | 1066 | 1185 | 1105 | 32 | 39
JIS B2202 | 2K | 923 | 1006 | 1095 | 1030 | 24 | 27
| 5K | 923 | 1000 | 1095 | 1030 | 24 | 33
| 10K | 923 | 1020 | 1120 | 1050 | 28 | 33
| 16K | 923 | 1045 | - | - | - | -
| 20K | 923 | 1088 | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | 919.2 | 1046.2 | 1168.4 | 1085.9 | 32 | 41.3
| Class D | 919.2 | 1046.2 | 1168.4 | 1085.9 | 32 | 41.3
| Class E | 919.2 | 1046.2 | 1168.4 | 1085.9 | 32 | 41.3
| Class F | 920.8 | 1116 | 1270 | 1168.4 | 32 | 54
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | 928 | - | 1115 | 1050 | 28 | 33
| PN16 | 928 | - | 1125 | 1050 | 28 | 39
| PN25 | 928 | - | 1185 | 1090 | 28 | 48
ISO7483 | PN2.5 | 915 | 990 | - | - | - | -
| PN6 | 915 | 990 | - | - | - | -
| PN10 | 915 | 1017 | 1115 | 1050 | 28 | 33
| PN16 | 915 | 1011 | 1125 | 1050 | 28 | 39
| PN20 | 914 | 1047 | - | - | - | -
| PN25 | 915 | 1042 | 1185 | 1090 | 28 | 48
| PN40 | - | - | - | - | - | -
| PN50 | 914 | 1116 | - | - | - | -
| PN110 | 914 | 1130 | - | - | - | -
| PN150 | 914 | 1199 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 950mm
38" / 950mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | 965 | 1111 | 1238.3 | 1149.4 | 32 | 41.1
| ASA300 | 965 | 1054 | 1168.4 | 1092.2 | 32 | 41.1
| ASA600 | 965 | 1105 | 1270 | 1162.1 | 28 | 60.5
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 965 | 1045 | 1124 | 1069.8 | 40 | 28.4
| ASA300 | 965 | 1099 | 1222.2 | 1140 | 36 | 44.5
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
Nominal Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
True Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | - | - | - | - | - | -
| 10K | - | - | - | - | - | -
| 16K | - | - | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | 970 | 1109.7 | 1238.3 | 1149.4 | 32 | 41.3
| Class D | 970 | 1109.7 | 1238.3 | 1149.4 | 32 | 41.3
| Class E | 970 | 1109.7 | 1238.3 | 1149.4 | 32 | 41.3
| Class F | 971.6 | 1166.8 | 1327.2 | 1219.2 | 32 | 54
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | 965 | 1111 | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | 965 | 1053 | - | - | - | -
| PN110 | 965 | 1106 | - | - | - | -
| PN150 | 965 | 1199 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 1000mm
40" / 1000mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | 1016 | 1162 | 1289.1 | 1200.2 | 36 | 41.1
| ASA300 | 1016 | 1114 | 1238.3 | 1155.7 | 32 | 44.5
| ASA600 | 1016 | 1156 | 1320.8 | 1212.9 | 32 | 60.5
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 1016 | 1095 | 1174.8 | 1120.6 | 44 | 28.4
| ASA300 | 1016 | 1149 | 1273 | 1190.8 | 40 | 44.5
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | 1041.4 | 1088 | 1180 | 1118 | 24 | 30
Nominal Bore | BST D | 1041.4 | 1139 | 1255 | 1175 | 24 | 36
| BST E | 1041.4 | 1136 | 1255 | 1175 | 24 | 39
| BST F | 1041.4 | 1155 | 1275 | 1194 | 36 | 39
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 1016 | 1088 | 1180 | 1118 | 24 | 30
True Bore | BST D | 1016 | 1139 | 1255 | 1175 | 24 | 36
| BST E | 1016 | 1136 | 1255 | 1175 | 24 | 39
| BST F | 1016 | 1155 | 1275 | 1194 | 36 | 39
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | 1020 | 1090 | 1175 | 1120 | 28 | 30
& DIN2690 | PN6 | 1020 | 1090 | 1175 | 1120 | 28 | 30
| PN10 | 1020 | 1120 | 1230 | 1160 | 28 | 36
| PN16 | 1020 | 1125 | 1255 | 1170 | 28 | 42
| PN25 | 1020 | 1150 | 1320 | 1210 | 28 | 56
| PN40 | 1020 | 1190 | 1360 | 1250 | 28 | 56
AS4087 | Class 14/16 | 1041.4 | 1139 | 1255 | 1175 | 24 | 36
| Class 21/35 | 1041.4 | 1155 | 1275 | 1194 | 36 | 39
JIS B2202 | 2K | 1025 | 1106 | 1195 | 1130 | 28 | 27
| 5K | 1025 | 1100 | 1195 | 1130 | 28 | 33
| 10K | 1025 | 1124 | 1235 | 1160 | 28 | 39
| 16K | 1025 | 1158 | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | 1020.8 | 1160.5 | 1289.1 | 1200.2 | 36 | 41.3
| Class D | 1020.8 | 1160.5 | 1289.1 | 1200.2 | 36 | 41.3
| Class E | 1020.8 | 1160.5 | 1289.1 | 1200.2 | 36 | 41.3
| Class F | 1022.4 | 1224 | 1378 | 1276.4 | 36 | 54
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | 1032 | - | 1230 | 1160 | 28 | 36
| PN16 | 1032 | - | 1255 | 1170 | 28 | 42
| PN25 | 1032 | - | 1320 | 1210 | 28 | 56
ISO7483 | PN2.5 | 1016 | 1090 | - | - | - | -
| PN6 | 1016 | 1090 | - | - | - | -
| PN10 | 1016 | 1124 | 1230 | 1160 | 28 | 36
| PN16 | 1016 | 1128 | 1255 | 1170 | 28 | 42
| PN20 | 1016 | 1161 | - | - | - | -
| PN25 | 1016 | 1154 | 1320 | 1210 | 28 | 55
| PN40 | - | - | - | - | - | -
| PN50 | 1016 | 1114 | - | - | - | -
| PN110 | 1016 | 1157 | - | - | - | -
| PN150 | 1016 | 1250 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 1050mm
42" / 1050mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | 1067 | 1219 | 1346 | 1257.3 | 36 | 41.3
Series A | ASA150 | 1067 | 1219 | 1346.2 | 1257.3 | 36 | 41.1
| ASA300 | 1067 | 1165 | 1289.1 | 1206.5 | 32 | 44.5
| ASA600 | 1067 | 1219 | 1403.4 | 1282.7 | 28 | 66.5
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 1067 | 1146 | 1225.6 | 1171.4 | 48 | 28.4
| ASA300 | 1067 | 1200 | 1333.5 | 1244.6 | 36 | 47.8
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
Nominal Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
True Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | - | - | - | - | - | -
| 10K | - | - | - | - | - | -
| 16K | - | - | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | 1071.6 | 1217.6 | 1346.2 | 1257.3 | 36 | 41.3
| Class D | 1071.6 | 1217.6 | 1346.2 | 1257.3 | 36 | 41.3
| Class E | 1071.6 | 1217.6 | 1346.2 | 1257.3 | 36 | 41.3
| Class F | 1073.2 | 1287.5 | 1447.8 | 1339.9 | 36 | 54
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | 1067 | 1218 | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | 1067 | 1164 | - | - | - | -
| PN110 | 1067 | 1219 | - | - | - | -
| PN150 | 1067 | 1301 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 1100mm
44" / 1100mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | 1118 | 1276 | 1403.4 | 1314.5 | 40 | 41.1
| ASA300 | 1118 | 1219 | 1352.6 | 1263.7 | 32 | 47.8
| ASA600 | 1118 | 1270 | 1454.2 | 1333.5 | 32 | 66.5
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 1118 | 1197 | 1276.4 | 1222.2 | 52 | 28.4
| ASA300 | 1118 | 1251 | 1384.3 | 1295.4 | 40 | 47.8
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
Nominal Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
True Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | 1130 | 1216 | 1305 | 1240 | 28 | 27
| 5K | 1130 | 1210 | 1305 | 1240 | 28 | 33
| 10K | 1130 | 1234 | 1345 | 1270 | 28 | 39
| 16K | 1130 | 1258 | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | 1122.4 | 1274.8 | 1403.4 | 1314.5 | 40 | 41.3
| Class D | 1122.4 | 1274.8 | 1403.4 | 1314.5 | 40 | 41.3
| Class E | 1122.4 | 1274.8 | 1403.4 | 1314.5 | 40 | 41.3
| Class F | 1124 | 1344.6 | 1505 | 1397 | 36 | 54
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | 1118 | 1275 | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | 1118 | 1219 | - | - | - | -
| PN110 | 1118 | 1270 | - | - | - | -
| PN150 | 1118 | 1369 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 1150mm
46" / 1150mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | 1168 | 1327 | 1454.2 | 1365.3 | 40 | 41.1
| ASA300 | 1168 | 1273 | 1416.1 | 1320.8 | 28 | 50.8
| ASA600 | 1168 | 1327 | 1511.3 | 1390.7 | 32 | 66.5
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 1168 | 1256 | 1341.4 | 1284.2 | 40 | 31.8
| ASA300 | 1168 | 1318 | 1460.5 | 1365.3 | 36 | 50.8
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
Nominal Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
True Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | - | - | - | - | - | -
| 10K | - | - | - | - | - | -
| 16K | - | - | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | 1173.2 | 1325.6 | 1454.2 | 1365.3 | 40 | 41.3
| Class E | 1173.2 | 1325.6 | 1454.2 | 1365.3 | 40 | 41.3
| Class F | 1174.8 | 1401.8 | 1562.1 | 1454.2 | 40 | 54
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | 1168 | 1326 | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | 1168 | 1273 | - | - | - | -
| PN110 | 1168 | 1327 | - | - | - | -
| PN150 | 1168 | 1437 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 1200mm
48" / 1200mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | 1219 | 1384 | 1511 | 1422.4 | 44 | 41.3
Series A | ASA150 | 1219 | 1384 | 1511.3 | 1422.4 | 44 | 41.1
| ASA300 | 1219 | 1324 | 1466.9 | 1371.6 | 32 | 50.8
| ASA600 | 1219 | 1391 | 1593.9 | 1460.5 | 32 | 73.2
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 1219 | 1307 | 1392.2 | 1335 | 44 | 31.8
| ASA300 | 1219 | 1368 | 1511.3 | 1416.1 | 40 | 50.8
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | 1244.6 | 1323 | 1415 | 1353 | 28 | 30
Nominal Bore | BST D | 1244.6 | 1374 | 1490 | 1410 | 32 | 36
| BST E | 1244.6 | 1371 | 1490 | 1410 | 32 | 39
| BST F | 1244.6 | 1399 | 1530 | 1441 | 40 | 42
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 1219 | 1323 | 1415 | 1353 | 28 | 30
True Bore | BST D | 1219 | 1374 | 1490 | 1410 | 32 | 36
| BST E | 1219 | 1371 | 1490 | 1410 | 32 | 39
| BST F | 1219 | 1399 | 1530 | 1441 | 40 | 42
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | 1220 | 1290 | 1375 | 1320 | 32 | 30
& DIN2690 | PN6 | 1220 | 1305 | 1405 | 1340 | 32 | 33
| PN10 | 1220 | 1340 | 1455 | 1380 | 32 | 39
| PN16 | 1220 | 1340 | 1485 | 1390 | 32 | 48
| PN25 | 1220 | 1360 | 1530 | 1420 | 30 | 56
| PN40 | 1220 | 1395 | 1575 | 1460 | 32 | 62
AS4087 | Class 14/16 | 1244.6 | 1374 | 1490 | 1410 | 32 | 36
| Class 21/35 | 1244.6 | 1399 | 1530 | 1441 | 40 | 42
JIS B2202 | 2K | 1230 | 1326 | 1420 | 1350 | 32 | 27
| 5K | 1230 | 1320 | 1420 | 1350 | 32 | 33
| 10K | 1230 | 1344 | 1465 | 1380 | 32 | 39
| 16K | 1230 | 1368 | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | 1224 | 1382.7 | 1511.3 | 1422.4 | 44 | 41.3
| Class E | 1224 | 1382.7 | 1511.3 | 1422.4 | 44 | 41.3
| Class F | 1225.6 | 1490.7 | 1651 | 1543.1 | 40 | 54
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | 1220 | - | 1455 | 1380 | 32 | 39
| PN16 | 1220 | - | 1485 | 1390 | 32 | 48
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | 1220 | 1290 | - | - | - | -
| PN6 | 1220 | 1307 | - | - | - | -
| PN10 | 1220 | 1341 | 1455 | 1380 | 32 | 39
| PN16 | 1220 | 1342 | 1485 | 1390 | 32 | 48
| PN20 | 1219 | 1383 | - | - | - | -
| PN25 | 1220 | 1365 | 1530 | 1420 | 32 | 55
| PN40 | - | - | - | - | - | -
| PN50 | 1219 | 1324 | - | - | - | -
| PN110 | 1219 | 1388 | - | - | - | -
| PN150 | 1219 | 1488 | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 1250mm
50" / 1250mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | 1270 | 1435 | 1568.5 | 1479.6 | 44 | 47.8
| ASA300 | 1270 | 1378 | 1530.4 | 1428.8 | 32 | 53.8
| ASA600 | 1270 | 1448 | 1670.1 | 1524 | 28 | 79.2
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 1270 | 1357 | 1443 | 1385.8 | 48 | 31.8
| ASA300 | 1270 | 1419 | 1562.1 | 1466.9 | 44 | 50.8
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
Nominal Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
True Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | - | - | - | - | - | -
| 10K | - | - | - | - | - | -
| 16K | - | - | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | 1274.8 | 1433.5 | 1568.5 | 1479.6 | 44 | 47.6
| Class E | 1274.8 | 1433.5 | 1568.5 | 1479.6 | 44 | 47.6
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | 1270 | 1435 | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | 1270 | 1377 | - | - | - | -
| PN110 | 1270 | 1448 | - | - | - | -
| PN150 | - | - | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 1300mm
52" / 1300mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | 1321 | 1492 | 1625.6 | 1536.7 | 44 | 47.8
| ASA300 | 1321 | 1429 | 1581.2 | 1479.6 | 32 | 53.8
| ASA600 | 1321 | 1499 | 1720.9 | 1574.8 | 32 | 79.2
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 1321 | 1408 | 1493.8 | 1436.6 | 52 | 31.8
| ASA300 | 1321 | 1470 | 1612.9 | 1517.7 | 48 | 50.8
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
Nominal Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
True Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | - | - | - | - | - | -
| 10K | - | - | - | - | - | -
| 16K | - | - | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | 1325.6 | 1490.7 | 1625.6 | 1536.7 | 44 | 47.6
| Class E | 1325.6 | 1490.7 | 1625.6 | 1536.7 | 44 | 47.6
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | 1321 | 1492 | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | 1321 | 1428 | - | - | - | -
| PN110 | 1321 | 1499 | - | - | - | -
| PN150 | - | - | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 1350mm
54" / 1350mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | 1372 | 1549 | 1682.8 | 1593.9 | 44 | 47.8
Series A | ASA150 | 1372 | 1549 | 1682.8 | 1593.9 | 44 | 47.8
| ASA300 | 1372 | 1492 | 1657.4 | 1549.4 | 28 | 60.5
| ASA600 | 1372 | 1556 | 1778 | 1632 | 32 | 79.2
ANSI B16.21 | ASA125 | 1372 | 1549 | 1682.8 | 1593.9 | 44 | 47.8
Series B | ASA150 | 1372 | 1464 | 1549.4 | 1492.3 | 56 | 31.8
| ASA300 | 1372 | 1530 | 1673.4 | 1577.8 | 48 | 50.8
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
Nominal Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
True Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | 1385 | 1481 | 1575 | 1505 | 32 | 27
| 5K | 1385 | 1475 | 1575 | 1505 | 32 | 33
| 10K | 1385 | 1498 | 1630 | 1540 | 36 | 45
| 16K | 1385 | 1534 | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | 1376.4 | 1547.8 | 1682.8 | 1593.9 | 44 | 47.6
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | 1372 | 1549 | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | 1372 | 1493 | - | - | - | -
| PN110 | 1372 | 1556 | - | - | - | -
| PN150 | - | - | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 1400mm
56" / 1400mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | 1422 | 1607 | 1746.3 | 1651 | 48 | 47.8
| ASA300 | 1422 | 1543 | 1708.2 | 1600.2 | 28 | 60.5
| ASA600 | 1422 | 1613 | 1854.2 | 1695.5 | 32 | 85.9
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 1422 | 1514 | 1600.2 | 1543.1 | 60 | 31.8
| ASA300 | 1422 | 1594 | 1765.3 | 1651 | 36 | 60.5
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | 1447.8 | 1579 | 1700 | 1615 | 32 | 36
Nominal Bore | BST D | 1447.8 | 1579 | 1700 | 1615 | 36 | 36
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 1422 | 1579 | 1700 | 1615 | 32 | 36
True Bore | BST D | 1422 | 1579 | 1700 | 1615 | 36 | 36
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | 1420 | 1490 | 1575 | 1520 | 36 | 30
& DIN2690 | PN6 | 1420 | 1520 | 1630 | 1560 | 36 | 36
| PN10 | 1420 | 1545 | 1675 | 1590 | 36 | 42
| PN16 | 1420 | 1540 | 1685 | 1590 | 36 | 48
| PN25 | 1420 | 1575 | 1755 | 1640 | 36 | 62
| PN40 | 1420 | 1615 | 1795 | 1680 | 36 | 62
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | - | - | - | - | - | -
| 10K | - | - | - | - | - | -
| 16K | - | - | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | 1420 | - | 1675 | 1590 | 36 | 42
| PN16 | 1420 | - | 1685 | 1590 | 36 | 48
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | 1420 | 1490 | - | - | - | -
| PN6 | 1420 | 1524 | - | - | - | -
| PN10 | 1420 | 1548 | 1675 | 1590 | 36 | 42
| PN16 | 1420 | 1542 | 1685 | 1590 | 36 | 48
| PN20 | 1422 | 1606 | - | - | - | -
| PN25 | 1420 | 1580 | 1755 | 1640 | 36 | 60
| PN40 | - | - | - | - | - | -
| PN50 | 1422 | 1544 | - | - | - | -
| PN110 | 1422 | 1615 | - | - | - | -
| PN150 | - | - | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 1450mm
58" / 1450mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | 1473 | 1664 | 1803.4 | 1708.2 | 48 | 47.8
| ASA300 | 1473 | 1594 | 1759 | 1651 | 32 | 60.5
| ASA600 | 1473 | 1664 | 1905 | 1746.3 | 32 | 85.9
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | 1473 | 1580 | 1674.9 | 1611.4 | 48 | 35.1
| ASA300 | 1473 | 1656 | 1827.3 | 1713 | 40 | 60.5
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
Nominal Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
True Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | - | - | - | - | - | -
| 10K | - | - | - | - | - | -
| 16K | - | - | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | 1473 | 1663 | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | 1473 | 1595 | - | - | - | -
| PN110 | 1473 | 1666 | - | - | - | -
| PN150 | - | - | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 1500mm
60" / 1500mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | 1524 | 1715 | 1854.2 | 1759 | 52 | 47.8
Series A | ASA150 | 1524 | 1715 | 1854.2 | 1759 | 52 | 47.8
| ASA300 | 1524 | 1645 | 1809.8 | 1701.8 | 32 | 60.5
| ASA600 | 1524 | 1721 | 1993.9 | 1822.5 | 28 | 91.9
ANSI B16.21 | ASA125 | 1524 | 1715 | 1854.2 | 1759 | 52 | 47.8
Series B | ASA150 | 1524 | 1630 | 1725.7 | 1662.2 | 52 | 35.1
| ASA300 | 1524 | 1705 | 1878.1 | 1763.8 | 40 | 60.5
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
Nominal Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
True Bore | BST D | - | - | - | - | - | -
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | - | - | - | - | - | -
& DIN2690 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | 1540 | 1636 | 1730 | 1660 | 27 | 36
| 5K | 1540 | 1630 | 1730 | 1660 | 33 | 36
| 10K | 1540 | 1658 | 1795 | 1700 | 45 | 40
| 16K | 1540 | 1694 | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
[5 empty] | - | - | -
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | - | - | - | - | - | -
| PN6 | - | - | - | - | - | -
| PN10 | - | - | - | - | - | -
| PN16 | - | - | - | - | - | -
| PN20 | 1524 | 1714 | - | - | - | -
| PN25 | - | - | - | - | - | -
| PN40 | - | - | - | - | - | -
| PN50 | 1524 | 1706 | - | - | - | -
| PN110 | 1524 | 1732 | - | - | - | -
| PN150 | - | - | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 1600mm
64" / 1600mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | - | - | - | - | - | -
| ASA300 | - | - | - | - | - | -
| ASA600 | - | - | - | - | - | -
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | - | - | - | - | - | -
| ASA300 | - | - | - | - | - | -
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | 1651 | 1789 | 1910 | 1825 | 32 | 36
Nominal Bore | BST D | 1651 | 1786 | 1910 | 1825 | 40 | 39
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 1625.6 | 1789 | 1910 | 1825 | 32 | 36
True Bore | BST D | 1625.6 | 1786 | 1910 | 1825 | 40 | 39
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | 1620 | 1700 | 1790 | 1730 | 40 | 30
& DIN2690 | PN6 | 1620 | 1720 | 1830 | 1760 | 40 | 36
| PN10 | 1620 | 1770 | 1915 | 1820 | 40 | 48
| PN16 | 1620 | 1760 | 1930 | 1820 | 40 | 56
| PN25 | 1620 | 1795 | 1975 | 1860 | 40 | 62
| PN40 | 1620 | 1830 | 2025 | 1900 | 40 | 70
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | - | - | - | - | - | -
| 10K | - | - | - | - | - | -
| 16K | - | - | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | 2020 | - | 2325 | 2230 | 48 | 48
| PN16 | 2020 | - | 2345 | 2230 | 48 | 62
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | 1620 | 1700 | - | - | - | -
| PN6 | 1620 | 1724 | - | - | - | -
| PN10 | 1620 | 1772 | 1915 | 1820 | 40 | 48
| PN16 | 1620 | 1765 | 1930 | 1820 | 40 | 55
| PN20 | - | - | - | - | - | -
| PN25 | 1620 | 1800 | 1975 | 1860 | 40 | 60
| PN40 | - | - | - | - | - | -
| PN50 | - | - | - | - | - | -
| PN110 | - | - | - | - | - | -
| PN150 | - | - | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 1800mm
72" / 1800mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | 1828.8 | 2051 | 2197.1 | 2095.5 | 60 | 47.7
Series A | ASA150 | - | - | - | - | - | -
| ASA300 | - | - | - | - | - | -
| ASA600 | - | - | - | - | - | -
ANSI B16.21 | ASA125 | 1828.8 | 2051 | 2197.1 | 2095.5 | 60 | 47.7
Series B | ASA150 | - | - | - | - | - | -
| ASA300 | - | - | - | - | - | -
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | 1860.6 | 1980 | 2110 | 2019 | 36 | 39
Nominal Bore | BST D | 1860.6 | 1977 | 2110 | 2019 | 44 | 42
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | 1828.8 | 1980 | 2110 | 2019 | 36 | 39
True Bore | BST D | 1828.8 | 1977 | 2110 | 2019 | 44 | 42
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | 1820 | 1900 | 1990 | 1930 | 44 | 30
& DIN2690 | PN6 | 1820 | 1930 | 2045 | 1970 | 44 | 39
| PN10 | 1820 | 1970 | 2115 | 2020 | 44 | 48
| PN16 | 1820 | 1960 | 2345 | 2230 | 44 | 56
| PN25 | 1820 | 2000 | 2195 | 2070 | 44 | 70
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | - | - | - | - | - | -
| 10K | - | - | - | - | - | -
| 16K | - | - | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | 1820 | - | 2115 | 2020 | 44 | 48
| PN16 | 1820 | - | 2130 | 2020 | 44 | 56
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | 1820 | 1900 | - | - | - | -
| PN6 | 1820 | 1931 | - | - | - | -
| PN10 | 1820 | 1972 | 2115 | 2020 | 44 | 48
| PN16 | 1820 | 1965 | 2130 | 2020 | 44 | 55
| PN20 | - | - | - | - | - | -
| PN25 | 1820 | 2002 | 2195 | 2070 | 44 | 68
| PN40 | - | - | - | - | - | -
| PN50 | - | - | - | - | - | -
| PN110 | - | - | - | - | - | -
| PN150 | - | - | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## 2000mm
80" / 2000mm Nominal Bore
Revision: 10th January 2008
The nominal bore in the header is for the pipe. The flanges could be nominal or true bore.
GASKET DIMENSIONS
Standard | Table | ID (mm) | OD(mm) (Ring) | OD(mm) (Fullface) | PCD (mm) | No. of Holes | Hole Dia (mm)
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series A | ASA150 | - | - | - | - | - | -
| ASA300 | - | - | - | - | - | -
| ASA600 | - | - | - | - | - | -
ANSI B16.21 | ASA125 | - | - | - | - | - | -
Series B | ASA150 | - | - | - | - | - | -
| ASA300 | - | - | - | - | - | -
| ASA600 | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
Nominal Bore | BST D | 2057.4 | 2208 | 2345 | 2250 | 44 | 42
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS3063 | BST A | - | - | - | - | - | -
True Bore | BST D | 2032 | 2208 | 2345 | 2250 | 44 | 42
| BST E | - | - | - | - | - | -
| BST F | - | - | - | - | - | -
| BST H | - | - | - | - | - | -
| BST J | - | - | - | - | - | -
| BST K | - | - | - | - | - | -
| BST R | - | - | - | - | - | -
BS EN 1514-1 | PN2.5 | 2020 | 2100 | 2190 | 2130 | 48 | 30
& DIN2690 | PN6 | 2020 | 2135 | 2265 | 2180 | 48 | 42
| PN10 | 2020 | 2180 | 2325 | 2230 | 48 | 48
| PN16 | 2020 | 2165 | 2345 | 2230 | 48 | 62
| PN25 | 2020 | 2230 | 2425 | 2300 | 48 | 70
| PN40 | - | - | - | - | - | -
AS4087 | Class 14/16 | - | - | - | - | - | -
| Class 21/35 | - | - | - | - | - | -
JIS B2202 | 2K | - | - | - | - | - | -
| 5K | - | - | - | - | - | -
| 10K | - | - | - | - | - | -
| 16K | - | - | - | - | - | -
| 20K | - | - | - | - | - | -
| 30K | - | - | - | - | - | -
| 40K | - | - | - | - | - | -
| 63K | - | - | - | - | - | -
AWWA C207-01 | Class B | - | - | - | - | - | -
| Class D | - | - | - | - | - | -
| Class E | - | - | - | - | - | -
| Class F | - | - | - | - | - | -
DIN 86071 | PN6 | - | - | - | - | - | -
| PN10 | 2020 | - | 2325 | 2230 | 48 | 48
| PN16 | 2020 | - | 2345 | 2230 | 48 | 62
| PN25 | - | - | - | - | - | -
ISO7483 | PN2.5 | 2020 | 2100 | - | - | - | -
| PN6 | 2020 | 2138 | - | - | - | -
| PN10 | 2020 | 2182 | 2325 | 2230 | 48 | 48
| PN16 | 2020 | 2170 | 2345 | 2230 | 48 | 60
| PN20 | - | - | - | - | - | -
| PN25 | 2020 | 2230 | 2425 | 2300 | 48 | 68
| PN40 | - | - | - | - | - | -
| PN50 | - | - | - | - | - | -
| PN110 | - | - | - | - | - | -
| PN150 | - | - | - | - | - | -
Dimensions are taken from the following standards, original copies of which are available at Yagoona site:
BS3063:1965 |  | Dimensions of gaskets to suit pipe flanges to BS10.
BS EN1514.1:1997 |  | Dimensions of gaskets for flanges to BS4504 & DIN 2501 (BS4865.1:1989 Replaced by BS EN 1514.1:1997).
BS3293:1960 |  | Carbon Steel Pipe Flanges (Over 24 inch nominal size) for the Petroleum Industry.
ANSIB16.21:1992 |  | Nonmetallic flat gaskets for pipe flanges to ANSI B16.5.
DIN2690:1966 |  | Sealings for flanges with plain contact faces for pipe flanges to DIN2501
JIS B2202:1984 |  | Dimensions for pipe flange facings for pipe flanges to JIS B2220
ISO7483:1991 |  | Dimensions of gaskets for use with flanges to ISO7005
ANSI B16.47:1990 Ser A |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly MSS SP-44
ANSI B16.47:1990 Ser B |  | Large Diameter Carbon Steel Flanges (Over 24 inch nominal size) - Formerly API 605
AWWA C207-01 |  | Steel Pipe Flanges for Waterworks Service - Sizes 4 in Through 144 in (Class B 86psi, Class D 175-150psi, Class E 275psi, Class F 300psi)

## BST A
BS3063 Table 'A'
Revision: 10th January 2008
GASKET DIMENSIONS
Pipe Size | ID | OD(RG) | OD(FF) | PCD | Holes | Size
1/2" / 15mm Nominal Bore | 21.4312 | 52.3875 | 95.25 | 66.675 | 4 | 14.2875
3/4" / 20mm Nominal Bore | 26.9875 | 58.7125 | 101.6 | 73 | 4 | 14.2875
1" / 25mm Nominal Bore | 34.1313 | 68.2625 | 114.3 | 82.55 | 4 | 14.2875
1-1/4" / 32mm Nominal Bore | 42.8625 | 73.025 | 120.65 | 87.3125 | 4 | 14.2875
1-1/2" / 40mm Nominal Bore | 48.4188 | 84.1375 | 133.35 | 98.425 | 4 | 14.2875
2" / 50mm Nominal Bore | 60.325 | 95.25 | 152.4 | 114.3 | 4 | 19.05
2-1/2" / 65mm Nominal Bore | 76.2 | 107.95 | 165.1 | 127 | 4 | 19.05
3" / 80mm Nominal Bore | 88.9 | 127 | 184.15 | 146.05 | 4 | 19.05
3-1/2" / 90mm Nominal Bore | 101.6 | 146.05 | 203.2 | 165.1 | 4 | 19.05
4" / 100mm Nominal Bore | 114.3 | 158.75 | 215.9 | 177.8 | 4 | 19.05
5" / 125mm Nominal Bore | 139.7 | 190.5 | 254 | 209.55 | 4 | 19.05
6" / 150mm Nominal Bore | 168.275 | 215.9 | 279.4 | 234.95 | 8 | 19.05
7" / 175mm Nominal Bore | 193.7 | 241.3 | 304.8 | 260.4 | 8 | 19.1
8" / 200mm Nominal Bore | 219.075 | 273.05 | 336.55 | 292.1 | 8 | 19.05
10" / 250mm Nominal Bore | 273.05 | 333.375 | 406.4 | 355.6 | 8 | 22.225
12" / 300mm Nominal Bore | 323.85 | 384.175 | 457.2 | 406.4 | 8 | 22.225
14" / 350mm Nominal Bore | 381 | 444.5 | 527.05 | 469.9 | 8 | 25.4
15" / 375mm Nominal Bore | - | - | - | - | - | -
16" / 400mm Nominal Bore | 431.8 | 495.3 | 577.85 | 520.7 | 12 | 25.4
18" / 450mm Nominal Bore | 482.6 | 558.8 | 641.35 | 584.2 | 12 | 25.4
20" / 500mm Nominal Bore | 533.4 | 615.95 | 704.85 | 641.35 | 12 | 25.4
22" / 550mm Nominal Bore | 584.2 | 669.925 | 762 | 698.5 | 12 | 28.575
24" / 600mm Nominal Bore | 635 | 727.075 | 825.5 | 755.65 | 12 | 28.575
26" / 650mm Nominal Bore | 685.8 | 751 | 845 | 781 | 16 | 30
28" / 700mm Nominal Bore | 736.6 | 776 | 870 | 806 | 16 | 30
30" / 750mm Nominal Bore | 787.4 | 853 | 945 | 883 | 20 | 30
32" / 800mm Nominal Bore | 838.2 | 910 | 1005 | 940 | 20 | 30
34" / 850mm Nominal Bore | 889 | 935 | 1030 | 965 | 20 | 30
36" / 900mm Nominal Bore | 939.8 | 1011 | 1105 | 1041 | 24 | 30
38" / 950mm Nominal Bore | - | - | - | - | - | -
40" / 1000mm Nominal Bore | 1041.4 | 1088 | 1180 | 1118 | 24 | 30
42" / 1050mm Nominal Bore | - | - | - | - | - | -
44" / 1100mm Nominal Bore | - | - | - | - | - | -
46" / 1150mm Nominal Bore | - | - | - | - | - | -
48" / 1200mm Nominal Bore | 1244.6 | 1323 | 1415 | 1353 | 28 | 30
50" / 1250mm Nominal Bore | - | - | - | - | - | -
52" / 1300mm Nominal Bore | - | - | - | - | - | -
54" / 1350mm Nominal Bore | - | - | - | - | - | -
56" / 1400mm Nominal Bore | 1447.8 | 1579 | 1700 | 1615 | 32 | 36
58" / 1450mm Nominal Bore | - | - | - | - | - | -
60" / 1500mm Nominal Bore | - | - | - | - | - | -

## BST D
BS3063 Table 'D'
Revision: 10th January 2008
GASKET DIMENSIONS
Pipe Size | ID | OD(RG) | OD(FF) | PCD | Holes | Size
1/2" / 15mm Nominal Bore | 21.4312 | 52.3875 | 95.25 | 66.675 | 4 | 14.2875
3/4" / 20mm Nominal Bore | 26.9875 | 58.7125 | 101.6 | 73 | 4 | 14.2875
1" / 25mm Nominal Bore | 34.1313 | 68.2625 | 114.3 | 82.55 | 4 | 14.2875
1-1/4" / 32mm Nominal Bore | 42.8625 | 73.025 | 120.65 | 87.3125 | 4 | 14.2875
1-1/2" / 40mm Nominal Bore | 48.4188 | 84.1375 | 133.35 | 98.425 | 4 | 14.2875
2" / 50mm Nominal Bore | 60.325 | 95.25 | 152.4 | 114.3 | 4 | 19.05
2-1/2" / 65mm Nominal Bore | 76.2 | 107.95 | 165.1 | 127 | 4 | 19.05
3" / 80mm Nominal Bore | 88.9 | 127 | 184.15 | 146.05 | 4 | 19.05
3-1/2" / 90mm Nominal Bore | 101.6 | 146.05 | 203.2 | 165.1 | 4 | 19.05
4" / 100mm Nominal Bore | 114.3 | 158.75 | 215.9 | 177.8 | 4 | 19.05
5" / 125mm Nominal Bore | 139.7 | 190.5 | 254 | 209.55 | 8 | 19.05
6" / 150mm Nominal Bore | 168.275 | 215.9 | 279.4 | 234.95 | 8 | 19.05
7" / 175mm Nominal Bore | 193.7 | 241.3 | 304.8 | 260.35 | 8 | 19.05
8" / 200mm Nominal Bore | 219.075 | 273.05 | 336.55 | 292.1 | 8 | 19.05
10" / 250mm Nominal Bore | 273.05 | 333.375 | 406.4 | 355.6 | 8 | 22.225
12" / 300mm Nominal Bore | 323.85 | 384.175 | 457.2 | 406.4 | 12 | 22.225
14" / 350mm Nominal Bore | 381 | 444.5 | 527.05 | 469.9 | 12 | 25.4
15" / 375mm Nominal Bore | 406.4 | 469.9 | 552.45 | 495.3 | 12 | 25.4
16" / 400mm Nominal Bore | 431.8 | 495.3 | 577.85 | 520.7 | 12 | 25.4
18" / 450mm Nominal Bore | 482.6 | 558.8 | 641.35 | 584.2 | 12 | 25.4
20" / 500mm Nominal Bore | 533.4 | 615.95 | 704.85 | 641.35 | 16 | 25.4
22" / 550mm Nominal Bore | 584.2 | 669.925 | 762 | 698.5 | 16 | 28.575
24" / 600mm Nominal Bore | 635 | 727.075 | 825.5 | 755.65 | 16 | 28.575
26" / 650mm Nominal Bore | - | - | - | - | - | -
28" / 700mm Nominal Bore | 736.6 | 815 | 910 | 845 | 20 | 30
30" / 750mm Nominal Bore | 787.4 | 894 | 995 | 927 | 20 | 33
32" / 800mm Nominal Bore | 838.2 | 948 | 1060 | 984 | 20 | 36
34" / 850mm Nominal Bore | 889 | 980 | 1090 | 1016 | 20 | 36
36" / 900mm Nominal Bore | 939.8 | 1056 | 1175 | 1092 | 24 | 36
38" / 950mm Nominal Bore | - | - | - | - | - | -
40" / 1000mm Nominal Bore | 1041.4 | 1139 | 1255 | 1175 | 24 | 36
42" / 1050mm Nominal Bore | - | - | - | - | - | -
44" / 1100mm Nominal Bore | - | - | - | - | - | -
46" / 1150mm Nominal Bore | - | - | - | - | - | -
48" / 1200mm Nominal Bore | 1244.6 | 1374 | 1490 | 1410 | 32 | 36
50" / 1250mm Nominal Bore | - | - | - | - | - | -
52" / 1300mm Nominal Bore | - | - | - | - | - | -
54" / 1350mm Nominal Bore | - | - | - | - | - | -
56" / 1400mm Nominal Bore | 1447.8 | 1579 | 1700 | 1615 | 36 | 36
58" / 1450mm Nominal Bore | - | - | - | - | - | -
60" / 1500mm Nominal Bore | - | - | - | - | - | -

## BST E
BS3063 Table 'E'
Revision: 10th January 2008
GASKET DIMENSIONS
Pipe Size | ID | OD(RG) | OD(FF) | PCD | Holes | Size
1/2" / 15mm Nominal Bore | 21.4312 | 52.3875 | 95.25 | 66.675 | 4 | 14.2875
3/4" / 20mm Nominal Bore | 26.9875 | 58.7125 | 101.6 | 73 | 4 | 14.2875
1" / 25mm Nominal Bore | 34.1313 | 68.2625 | 114.3 | 82.55 | 4 | 14.2875
1-1/4" / 32mm Nominal Bore | 42.8625 | 73.025 | 120.65 | 87.3125 | 4 | 14.2875
1-1/2" / 40mm Nominal Bore | 48.4188 | 84.1375 | 133.35 | 98.425 | 4 | 14.2875
2" / 50mm Nominal Bore | 60.325 | 95.25 | 152.4 | 114.3 | 4 | 19.05
2-1/2" / 65mm Nominal Bore | 76.2 | 107.95 | 165.1 | 127 | 4 | 19.05
3" / 80mm Nominal Bore | 88.9 | 127 | 184.15 | 146.05 | 4 | 19.05
3-1/2" / 90mm Nominal Bore | 101.6 | 146.05 | 203.2 | 165.1 | 8 | 19.05
4" / 100mm Nominal Bore | 114.3 | 158.75 | 215.9 | 177.8 | 8 | 19.05
5" / 125mm Nominal Bore | 139.7 | 190.5 | 254 | 209.55 | 8 | 19.05
6" / 150mm Nominal Bore | 168.275 | 212.725 | 279.4 | 234.95 | 8 | 22.225
7" / 175mm Nominal Bore | 193.7 | 238.125 | 304.8 | 260.35 | 8 | 22.225
8" / 200mm Nominal Bore | 219.075 | 269.875 | 336.55 | 292.1 | 8 | 22.225
10" / 250mm Nominal Bore | 273.05 | 333.375 | 406.4 | 355.6 | 12 | 22.225
12" / 300mm Nominal Bore | 323.85 | 380.4 | 457.2 | 406.4 | 12 | 26
14" / 350mm Nominal Bore | 381 | 444.5 | 527.05 | 469.9 | 12 | 25.4
15" / 375mm Nominal Bore | 406.4 | 469.9 | 552.45 | 495.3 | 12 | 25.4
16" / 400mm Nominal Bore | 431.8 | 495.3 | 577.85 | 520.7 | 12 | 25.4
18" / 450mm Nominal Bore | 482.6 | 558.8 | 641.35 | 584.2 | 16 | 25.4
20" / 500mm Nominal Bore | 533.4 | 615.95 | 704.85 | 641.35 | 16 | 25.4
22" / 550mm Nominal Bore | 584.2 | 669.925 | 762 | 698.5 | 16 | 28.575
24" / 600mm Nominal Bore | 635 | 722.65 | 825.5 | 755.65 | 16 | 33
26" / 650mm Nominal Bore | - | - | - | - | - | -
28" / 700mm Nominal Bore | 736.6 | 812 | 910 | 845 | 20 | 33
30" / 750mm Nominal Bore | 787.4 | 891 | 995 | 927 | 20 | 36
32" / 800mm Nominal Bore | 838.2 | 948 | 1060 | 984 | 20 | 36
34" / 850mm Nominal Bore | 889 | 980 | 1090 | 1016 | 20 | 36
36" / 900mm Nominal Bore | 939.8 | 1056 | 1175 | 1092 | 24 | 36
38" / 950mm Nominal Bore | - | - | - | - | - | -
40" / 1000mm Nominal Bore | 1041.4 | 1136 | 1255 | 1175 | 24 | 39
42" / 1050mm Nominal Bore | - | - | - | - | - | -
44" / 1100mm Nominal Bore | - | - | - | - | - | -
46" / 1150mm Nominal Bore | - | - | - | - | - | -
48" / 1200mm Nominal Bore | 1244.6 | 1371 | 1490 | 1410 | 32 | 39
50" / 1250mm Nominal Bore | - | - | - | - | - | -
52" / 1300mm Nominal Bore | - | - | - | - | - | -
54" / 1350mm Nominal Bore | - | - | - | - | - | -
56" / 1400mm Nominal Bore | - | - | - | - | - | -
58" / 1450mm Nominal Bore | - | - | - | - | - | -
60" / 1500mm Nominal Bore | - | - | - | - | - | -

## Class150
ASME B16.21& B16.47(Series'A') Class150
Revision: 10th January 2008
GASKET DIMENSIONS
Pipe Size | ID | OD(RG) | OD(FF) | PCD | Holes | Size
1/2" / 15mm Nominal Bore | 21.336 | 47.752 | 88.9 | 60.452 | 4 | 15.748
3/4" / 20mm Nominal Bore | 26.924 | 57.15 | 98.552 | 69.85 | 4 | 15.748
1" / 25mm Nominal Bore | 33.274 | 66.548 | 107.95 | 79.248 | 4 | 15.748
1-1/4" / 32mm Nominal Bore | 42.164 | 76.2 | 117.348 | 88.9 | 4 | 15.748
1-1/2" / 40mm Nominal Bore | 48.514 | 85.852 | 127 | 98.552 | 4 | 15.748
2" / 50mm Nominal Bore | 60.452 | 104.648 | 152.4 | 120.65 | 4 | 19.05
2-1/2" / 65mm Nominal Bore | 73.152 | 123.952 | 177.8 | 139.7 | 4 | 19.05
3" / 80mm Nominal Bore | 88.9 | 136.652 | 190.5 | 152.4 | 4 | 19.05
3-1/2" / 90mm Nominal Bore | 101.6 | 162.052 | 215.9 | 177.8 | 8 | 19.05
4" / 100mm Nominal Bore | 114.3 | 174.752 | 228.6 | 190.5 | 8 | 19.05
5" / 125mm Nominal Bore | 141.224 | 196.85 | 254 | 215.9 | 8 | 22.352
6" / 150mm Nominal Bore | 168.148 | 222.25 | 279.4 | 241.3 | 8 | 22.352
7" / 175mm Nominal Bore | - | - | - | - | - | -
8" / 200mm Nominal Bore | 218.948 | 279.4 | 342.9 | 298.45 | 8 | 22.352
10" / 250mm Nominal Bore | 273.05 | 339.852 | 406.4 | 361.95 | 12 | 25.4
12" / 300mm Nominal Bore | 323.85 | 409.448 | 482.6 | 431.8 | 12 | 25.4
14" / 350mm Nominal Bore | 355.6 | 450.85 | 533.4 | 476.25 | 12 | 28.448
15" / 375mm Nominal Bore | - | - | - | - | - | -
16" / 400mm Nominal Bore | 406.4 | 514.35 | 596.9 | 539.75 | 16 | 28.448
18" / 450mm Nominal Bore | 457.2 | 549.148 | 635 | 577.85 | 16 | 31.75
20" / 500mm Nominal Bore | 508 | 606.552 | 698.5 | 635 | 20 | 31.75
22" / 550mm Nominal Bore | 559 | 660 | 749.3 | 692.2 | 20 | 34.9
24" / 600mm Nominal Bore | 609.6 | 717.55 | 812.8 | 749.3 | 20 | 35.052
Series A
26" / 650mm Nominal Bore | 660 | 775 | 870 | 806.5 | 24 | 35.1
28" / 700mm Nominal Bore | 711 | 832 | 927.1 | 863.6 | 28 | 35.1
30" / 750mm Nominal Bore | 762 | 883 | 984.3 | 914.4 | 28 | 35.1
32" / 800mm Nominal Bore | 813 | 940 | 1060.5 | 977.9 | 28 | 41.1
34" / 850mm Nominal Bore | 864 | 991 | 1111.3 | 1028.7 | 32 | 41.1
36" / 900mm Nominal Bore | 914 | 1048 | 1168.4 | 1085.9 | 32 | 41.1
38" / 950mm Nominal Bore | 965 | 1111 | 1238.3 | 1149.4 | 32 | 41.1
40" / 1000mm Nominal Bore | 1016 | 1162 | 1289.1 | 1200.2 | 36 | 41.1
42" / 1050mm Nominal Bore | 1067 | 1219 | 1346.2 | 1257.3 | 36 | 41.1
44" / 1100mm Nominal Bore | 1118 | 1276 | 1403.4 | 1314.5 | 40 | 41.1
46" / 1150mm Nominal Bore | 1168 | 1327 | 1454.2 | 1365.3 | 40 | 41.1
48" / 1200mm Nominal Bore | 1219 | 1384 | 1511.3 | 1422.4 | 44 | 41.1
50" / 1250mm Nominal Bore | 1270 | 1435 | 1568.5 | 1479.6 | 44 | 47.8
52" / 1300mm Nominal Bore | 1321 | 1492 | 1625.6 | 1536.7 | 44 | 47.8
54" / 1350mm Nominal Bore | 1372 | 1549 | 1682.8 | 1593.9 | 44 | 47.8
56" / 1400mm Nominal Bore | 1422 | 1607 | 1746.3 | 1651 | 48 | 47.8
58" / 1450mm Nominal Bore | 1473 | 1664 | 1803.4 | 1708.2 | 48 | 47.8
60" / 1500mm Nominal Bore | 1524 | 1715 | 1854.2 | 1759 | 52 | 47.8

## Class300
ASME B16.21& B16.47(Series'A') Class300
Revision: 10th January 2008
GASKET DIMENSIONS
Pipe Size | ID | OD(RG) | OD(FF) | PCD | Holes | Size
1/2" / 15mm Nominal Bore | 21.336 | 53.848 | 95.25 | 66.548 | 4 | 15.748
3/4" / 20mm Nominal Bore | 26.924 | 66.548 | 117.348 | 82.55 | 4 | 19.05
1" / 25mm Nominal Bore | 33.274 | 73.152 | 123.952 | 88.9 | 4 | 19.05
1-1/4" / 32mm Nominal Bore | 42.164 | 82.55 | 133.35 | 98.552 | 4 | 19.05
1-1/2" / 40mm Nominal Bore | 48.514 | 95.25 | 155.448 | 114.3 | 4 | 22.352
2" / 50mm Nominal Bore | 60.452 | 111.252 | 165.1 | 127 | 8 | 19.05
2-1/2" / 65mm Nominal Bore | 73.152 | 130.048 | 190.5 | 149.352 | 8 | 22.352
3" / 80mm Nominal Bore | 88.9 | 149.352 | 209.55 | 168.148 | 8 | 22.352
3-1/2" / 90mm Nominal Bore | 101.6 | 165.1 | 228.6 | 184.15 | 8 | 22.352
4" / 100mm Nominal Bore | 114.3 | 180.848 | 254 | 200.152 | 8 | 22.352
5" / 125mm Nominal Bore | 141.224 | 215.9 | 279.4 | 234.95 | 8 | 22.352
6" / 150mm Nominal Bore | 168.148 | 250.952 | 317.5 | 269.748 | 12 | 22.352
7" / 175mm Nominal Bore | - | - | - | - | - | -
8" / 200mm Nominal Bore | 218.948 | 307.848 | 381 | 330.2 | 12 | 25.4
10" / 250mm Nominal Bore | 273.05 | 361.95 | 444.5 | 387.35 | 16 | 28.448
12" / 300mm Nominal Bore | 323.85 | 422.148 | 520.7 | 450.85 | 16 | 31.75
14" / 350mm Nominal Bore | 355.6 | 485.648 | 584.2 | 514.35 | 20 | 31.75
15" / 375mm Nominal Bore | - | - | - | - | - | -
16" / 400mm Nominal Bore | 406.4 | 539.75 | 647.7 | 571.5 | 20 | 35.052
18" / 450mm Nominal Bore | 457.2 | 596.9 | 711.2 | 628.65 | 24 | 35.052
20" / 500mm Nominal Bore | 508 | 654.05 | 774.7 | 685.8 | 24 | 35.052
22" / 550mm Nominal Bore | 559 | 705 | - | - | - | -
24" / 600mm Nominal Bore | 609.6 | 774.7 | 914.4 | 812.8 | 24 | 41.148
Series A
26" / 650mm Nominal Bore | 660 | 835 | 971.6 | 876.3 | 28 | 44.5
28" / 700mm Nominal Bore | 711 | 899 | 1035.1 | 939.8 | 28 | 44.5
30" / 750mm Nominal Bore | 762 | 953 | 1092.2 | 997 | 28 | 47.8
32" / 800mm Nominal Bore | 813 | 1006 | 1149.4 | 1054.1 | 28 | 50.8
34" / 850mm Nominal Bore | 864 | 1057 | 1206.5 | 1104.9 | 28 | 50.8
36" / 900mm Nominal Bore | 914 | 1118 | 1270 | 1168.4 | 32 | 53.8
38" / 950mm Nominal Bore | 965 | 1054 | 1168.4 | 1092.2 | 32 | 41.1
40" / 1000mm Nominal Bore | 1016 | 1114 | 1238.3 | 1155.7 | 32 | 44.5
42" / 1050mm Nominal Bore | 1067 | 1165 | 1289.1 | 1206.5 | 32 | 44.5
44" / 1100mm Nominal Bore | 1118 | 1219 | 1352.6 | 1263.7 | 32 | 47.8
46" / 1150mm Nominal Bore | 1168 | 1273 | 1416.1 | 1320.8 | 28 | 50.8
48" / 1200mm Nominal Bore | 1219 | 1324 | 1466.9 | 1371.6 | 32 | 50.8
50" / 1250mm Nominal Bore | 1270 | 1378 | 1530.4 | 1428.8 | 32 | 53.8
52" / 1300mm Nominal Bore | 1321 | 1429 | 1581.2 | 1479.6 | 32 | 53.8
54" / 1350mm Nominal Bore | 1372 | 1492 | 1657.4 | 1549.4 | 28 | 60.5
56" / 1400mm Nominal Bore | 1422 | 1543 | 1708.2 | 1600.2 | 28 | 60.5
58" / 1450mm Nominal Bore | 1473 | 1594 | 1759 | 1651 | 32 | 60.5
60" / 1500mm Nominal Bore | 1524 | 1645 | 1809.8 | 1701.8 | 32 | 60.5

## DIN2690 PN2.5
BS EN1514-1 & DIN2690 PN2.5
Revision: 10th January 2008
GASKET DIMENSIONS
Pipe Size | ID | OD(RG) | OD(FF) | PCD | Holes | Size
1/2" / 15mm Nominal Bore | 22 | 43 | 80 | 55 | 4 | 11
3/4" / 20mm Nominal Bore | 28 | 53 | 90 | 65 | 4 | 11
1" / 25mm Nominal Bore | 35 | 63 | 100 | 75 | 4 | 11
1-1/4" / 32mm Nominal Bore | 43 | 75 | 120 | 90 | 4 | 14
1-1/2" / 40mm Nominal Bore | 49 | 85 | 130 | 100 | 4 | 14
2" / 50mm Nominal Bore | 61 | 95 | 140 | 110 | 4 | 14
2-1/2" / 65mm Nominal Bore | 77 | 115 | 160 | 130 | 4 | 14
3" / 80mm Nominal Bore | 90 | 132 | 190 | 150 | 4 | 18
3-1/2" / 90mm Nominal Bore | - | - | - | - | - | -
4" / 100mm Nominal Bore | 115 | 152 | 210 | 170 | 4 | 18
5" / 125mm Nominal Bore | 141 | 182 | 240 | 200 | 8 | 18
6" / 150mm Nominal Bore | 169 | 207 | 265 | 225 | 8 | 18
7" / 175mm Nominal Bore | 195 | 237 | - | - | - | -
8" / 200mm Nominal Bore | 220 | 262 | 320 | 280 | 8 | 18
10" / 250mm Nominal Bore | 274 | 318 | 375 | 335 | 12 | 18
12" / 300mm Nominal Bore | 325 | 373 | 440 | 395 | 12 | 22
14" / 350mm Nominal Bore | 368 | 423 | 490 | 445 | 12 | 22
15" / 375mm Nominal Bore | - | - | - | - | - | -
16" / 400mm Nominal Bore | 420 | 473 | 540 | 495 | 16 | 22
18" / 450mm Nominal Bore | 470 | 528 | 595 | 550 | 16 | 22
20" / 500mm Nominal Bore | 520 | 578 | 645 | 600 | 20 | 22
22" / 550mm Nominal Bore | - | - | - | - | - | -
24" / 600mm Nominal Bore | 620 | 680 | 755 | 705 | 20 | 26
26" / 650mm Nominal Bore | - | - | - | - | - | -
28" / 700mm Nominal Bore | 720 | 785 | 860 | 810 | 24 | 26
30" / 750mm Nominal Bore | - | - | - | - | - | -
32" / 800mm Nominal Bore | 820 | 890 | 975 | 920 | 24 | 30
34" / 850mm Nominal Bore | - | - | - | - | - | -
36" / 900mm Nominal Bore | 920 | 990 | 1072 | 1020 | 24 | 30
38" / 950mm Nominal Bore | - | - | - | - | - | -
40" / 1000mm Nominal Bore | 1020 | 1090 | 1175 | 1120 | 28 | 30
42" / 1050mm Nominal Bore | - | - | - | - | - | -
44" / 1100mm Nominal Bore | - | - | - | - | - | -
46" / 1150mm Nominal Bore | - | - | - | - | - | -
48" / 1200mm Nominal Bore | 1220 | 1290 | 1375 | 1320 | 32 | 30
50" / 1250mm Nominal Bore | - | - | - | - | - | -
52" / 1300mm Nominal Bore | - | - | - | - | - | -
54" / 1350mm Nominal Bore | - | - | - | - | - | -
56" / 1400mm Nominal Bore | 1420 | 1490 | 1575 | 1520 | 36 | 30
58" / 1450mm Nominal Bore | - | - | - | - | - | -
60" / 1500mm Nominal Bore | - | - | - | - | - | -

## DIN2690 PN6
BS EN1514-1 & DIN2690 PN6
Revision: 10th January 2008
GASKET DIMENSIONS
Pipe Size | ID | OD(RG) | OD(FF) | PCD | Holes | Size
1/2" / 15mm Nominal Bore | 22 | 43 | 80 | 55 | 4 | 11
3/4" / 20mm Nominal Bore | 28 | 53 | 90 | 65 | 4 | 11
1" / 25mm Nominal Bore | 35 | 63 | 100 | 75 | 4 | 11
1-1/4" / 32mm Nominal Bore | 43 | 75 | 120 | 90 | 4 | 14
1-1/2" / 40mm Nominal Bore | 49 | 85 | 130 | 100 | 4 | 14
2" / 50mm Nominal Bore | 61 | 95 | 140 | 110 | 4 | 14
2-1/2" / 65mm Nominal Bore | 77 | 115 | 160 | 130 | 4 | 14
3" / 80mm Nominal Bore | 90 | 132 | 190 | 150 | 4 | 18
3-1/2" / 90mm Nominal Bore | - | - | - | - | - | -
4" / 100mm Nominal Bore | 115 | 152 | 210 | 170 | 4 | 18
5" / 125mm Nominal Bore | 141 | 182 | 240 | 200 | 8 | 18
6" / 150mm Nominal Bore | 169 | 207 | 265 | 225 | 8 | 18
7" / 175mm Nominal Bore | 195 | 237 | - | - | - | -
8" / 200mm Nominal Bore | 220 | 262 | 320 | 280 | 8 | 18
10" / 250mm Nominal Bore | 274 | 318 | 375 | 335 | 12 | 18
12" / 300mm Nominal Bore | 325 | 373 | 440 | 395 | 12 | 22
14" / 350mm Nominal Bore | 368 | 423 | 490 | 445 | 12 | 22
15" / 375mm Nominal Bore | - | - | - | - | - | -
16" / 400mm Nominal Bore | 420 | 473 | 540 | 495 | 16 | 22
18" / 450mm Nominal Bore | 470 | 528 | 595 | 550 | 16 | 22
20" / 500mm Nominal Bore | 520 | 578 | 645 | 600 | 20 | 22
22" / 550mm Nominal Bore | - | - | - | - | - | -
24" / 600mm Nominal Bore | 620 | 680 | 755 | 705 | 20 | 26
26" / 650mm Nominal Bore | - | - | - | - | - | -
28" / 700mm Nominal Bore | 720 | 785 | 860 | 810 | 24 | 26
30" / 750mm Nominal Bore | - | - | - | - | - | -
32" / 800mm Nominal Bore | 820 | 890 | 975 | 920 | 24 | 30
34" / 850mm Nominal Bore | - | - | - | - | - | -
36" / 900mm Nominal Bore | 920 | 990 | 1075 | 1020 | 24 | 30
38" / 950mm Nominal Bore | - | - | - | - | - | -
40" / 1000mm Nominal Bore | 1020 | 1090 | 1175 | 1120 | 28 | 30
42" / 1050mm Nominal Bore | - | - | - | - | - | -
44" / 1100mm Nominal Bore | - | - | - | - | - | -
46" / 1150mm Nominal Bore | - | - | - | - | - | -
48" / 1200mm Nominal Bore | 1220 | 1305 | 1405 | 1340 | 32 | 33
50" / 1250mm Nominal Bore | - | - | - | - | - | -
52" / 1300mm Nominal Bore | - | - | - | - | - | -
54" / 1350mm Nominal Bore | - | - | - | - | - | -
56" / 1400mm Nominal Bore | 1420 | 1520 | 1630 | 1560 | 36 | 36
58" / 1450mm Nominal Bore | - | - | - | - | - | -
60" / 1500mm Nominal Bore | - | - | - | - | - | -

## DIN2690 PN10
BS EN1514-1 & DIN2690 PN10
Revision: 10th January 2008
GASKET DIMENSIONS
Pipe Size | ID | OD(RG) | OD(FF) | PCD | Holes | Size
1/2" / 15mm Nominal Bore | 22 | 50 | 95 | 65 | 4 | 14
3/4" / 20mm Nominal Bore | 28 | 60 | 105 | 75 | 4 | 14
1" / 25mm Nominal Bore | 35 | 70 | 115 | 85 | 4 | 14
1-1/4" / 32mm Nominal Bore | 43 | 82 | 140 | 100 | 4 | 18
1-1/2" / 40mm Nominal Bore | 49 | 92 | 150 | 110 | 4 | 18
2" / 50mm Nominal Bore | 61 | 107 | 165 | 125 | 4 | 18
2-1/2" / 65mm Nominal Bore | 77 | 127 | 185 | 145 | 4 | 18
3" / 80mm Nominal Bore | 90 | 142 | 200 | 160 | 8 | 18
3-1/2" / 90mm Nominal Bore | - | - | - | - | - | -
4" / 100mm Nominal Bore | 115 | 162 | 220 | 180 | 8 | 18
5" / 125mm Nominal Bore | 141 | 192 | 250 | 210 | 8 | 18
6" / 150mm Nominal Bore | 169 | 218 | 285 | 240 | 8 | 22
7" / 175mm Nominal Bore | 195 | 248 | 315 | 270 | 8 | 22
8" / 200mm Nominal Bore | 220 | 273 | 340 | 295 | 8 | 22
10" / 250mm Nominal Bore | 274 | 328 | 395 | 350 | 12 | 22
12" / 300mm Nominal Bore | 325 | 378 | 445 | 400 | 12 | 22
14" / 350mm Nominal Bore | 368 | 438 | 505 | 460 | 16 | 22
15" / 375mm Nominal Bore | - | - | - | - | - | -
16" / 400mm Nominal Bore | 420 | 490 | 565 | 515 | 16 | 26
18" / 450mm Nominal Bore | 470 | 540 | 615 | 565 | 20 | 26
20" / 500mm Nominal Bore | 520 | 595 | 670 | 620 | 20 | 26
22" / 550mm Nominal Bore | - | - | - | - | - | -
24" / 600mm Nominal Bore | 620 | 695 | 780 | 725 | 20 | 30
26" / 650mm Nominal Bore | - | - | - | - | - | -
28" / 700mm Nominal Bore | 720 | 810 | 895 | 840 | 24 | 30
30" / 750mm Nominal Bore | - | - | - | - | - | -
32" / 800mm Nominal Bore | 820 | 915 | 1015 | 950 | 24 | 33
34" / 850mm Nominal Bore | - | - | - | - | - | -
36" / 900mm Nominal Bore | 920 | 1015 | 1115 | 1050 | 28 | 33
38" / 950mm Nominal Bore | - | - | - | - | - | -
40" / 1000mm Nominal Bore | 1020 | 1120 | 1230 | 1160 | 28 | 36
42" / 1050mm Nominal Bore | - | - | - | - | - | -
44" / 1100mm Nominal Bore | - | - | - | - | - | -
46" / 1150mm Nominal Bore | - | - | - | - | - | -
48" / 1200mm Nominal Bore | 1220 | 1340 | 1455 | 1380 | 32 | 39
50" / 1250mm Nominal Bore | - | - | - | - | - | -
52" / 1300mm Nominal Bore | - | - | - | - | - | -
54" / 1350mm Nominal Bore | - | - | - | - | - | -
56" / 1400mm Nominal Bore | 1420 | 1545 | 1675 | 1590 | 36 | 42
58" / 1450mm Nominal Bore | - | - | - | - | - | -
60" / 1500mm Nominal Bore | - | - | - | - | - | -

## DIN2690 PN16
BS EN1514-1 & DIN2690 PN16
Revision: 10th January 2008
GASKET DIMENSIONS
Pipe Size | ID | OD(RG) | OD(FF) | PCD | Holes | Size
1/2" / 15mm Nominal Bore | 22 | 50 | 95 | 65 | 4 | 14
3/4" / 20mm Nominal Bore | 28 | 60 | 105 | 75 | 4 | 14
1" / 25mm Nominal Bore | 35 | 70 | 115 | 85 | 4 | 14
1-1/4" / 32mm Nominal Bore | 43 | 82 | 140 | 100 | 4 | 18
1-1/2" / 40mm Nominal Bore | 49 | 92 | 150 | 110 | 4 | 18
2" / 50mm Nominal Bore | 61 | 107 | 165 | 125 | 4 | 18
2-1/2" / 65mm Nominal Bore | 77 | 127 | 185 | 145 | 4 | 18
3" / 80mm Nominal Bore | 90 | 142 | 200 | 160 | 8 | 18
3-1/2" / 90mm Nominal Bore | - | - | - | - | - | -
4" / 100mm Nominal Bore | 115 | 162 | 220 | 180 | 8 | 18
5" / 125mm Nominal Bore | 141 | 192 | 250 | 210 | 8 | 18
6" / 150mm Nominal Bore | 169 | 218 | 285 | 240 | 8 | 22
7" / 175mm Nominal Bore | 195 | 248 | 315 | 270 | 8 | 22
8" / 200mm Nominal Bore | 220 | 273 | 340 | 295 | 12 | 22
10" / 250mm Nominal Bore | 274 | 330 | 405 | 355 | 12 | 26
12" / 300mm Nominal Bore | 325 | 385 | 460 | 410 | 12 | 26
14" / 350mm Nominal Bore | 368 | 445 | 520 | 470 | 16 | 26
15" / 375mm Nominal Bore | - | - | - | - | - | -
16" / 400mm Nominal Bore | 420 | 497 | 580 | 525 | 16 | 30
18" / 450mm Nominal Bore | 470 | 557 | 640 | 585 | 20 | 30
20" / 500mm Nominal Bore | 520 | 618 | 715 | 650 | 20 | 33
22" / 550mm Nominal Bore | - | - | - | - | - | -
24" / 600mm Nominal Bore | 620 | 735 | 840 | 770 | 20 | 36
26" / 650mm Nominal Bore | - | - | - | - | - | -
28" / 700mm Nominal Bore | 720 | 805 | 910 | 840 | 24 | 36
30" / 750mm Nominal Bore | - | - | - | - | - | -
32" / 800mm Nominal Bore | 820 | 910 | 1025 | 950 | 24 | 39
34" / 850mm Nominal Bore | - | - | - | - | - | -
36" / 900mm Nominal Bore | 920 | 1010 | 1125 | 1050 | 28 | 39
38" / 950mm Nominal Bore | - | - | - | - | - | -
40" / 1000mm Nominal Bore | 1020 | 1125 | 1255 | 1170 | 28 | 42
42" / 1050mm Nominal Bore | - | - | - | - | - | -
44" / 1100mm Nominal Bore | - | - | - | - | - | -
46" / 1150mm Nominal Bore | - | - | - | - | - | -
48" / 1200mm Nominal Bore | 1220 | 1340 | 1485 | 1390 | 32 | 48
50" / 1250mm Nominal Bore | - | - | - | - | - | -
52" / 1300mm Nominal Bore | - | - | - | - | - | -
54" / 1350mm Nominal Bore | - | - | - | - | - | -
56" / 1400mm Nominal Bore | 1420 | 1540 | 1685 | 1590 | 36 | 48
58" / 1450mm Nominal Bore | - | - | - | - | - | -
60" / 1500mm Nominal Bore | - | - | - | - | - | -

## DIN2690 PN25
BS EN1514-1 & DIN2690 PN25
Revision: 10th January 2008
GASKET DIMENSIONS
Pipe Size | ID | OD(RG) | OD(FF) | PCD | Holes | Size
1/2" / 15mm Nominal Bore | 22 | 50 | 95 | 65 | 4 | 14
3/4" / 20mm Nominal Bore | 28 | 60 | 105 | 75 | 4 | 14
1" / 25mm Nominal Bore | 35 | 70 | 115 | 85 | 4 | 14
1-1/4" / 32mm Nominal Bore | 43 | 82 | 140 | 100 | 4 | 18
1-1/2" / 40mm Nominal Bore | 49 | 92 | 150 | 110 | 4 | 18
2" / 50mm Nominal Bore | 61 | 107 | 165 | 125 | 4 | 18
2-1/2" / 65mm Nominal Bore | 77 | 127 | 185 | 145 | 8 | 18
3" / 80mm Nominal Bore | 90 | 142 | 200 | 160 | 8 | 18
3-1/2" / 90mm Nominal Bore | - | - | - | - | - | -
4" / 100mm Nominal Bore | 115 | 168 | 235 | 190 | 8 | 22
5" / 125mm Nominal Bore | 141 | 195 | 270 | 220 | 8 | 26
6" / 150mm Nominal Bore | 169 | 225 | 300 | 250 | 8 | 26
7" / 175mm Nominal Bore | 195 | 255 | 330 | 280 | 12 | 26
8" / 200mm Nominal Bore | 220 | 285 | 360 | 310 | 12 | 26
10" / 250mm Nominal Bore | 274 | 342 | 425 | 370 | 12 | 30
12" / 300mm Nominal Bore | 325 | 402 | 485 | 430 | 16 | 30
14" / 350mm Nominal Bore | 368 | 458 | 555 | 490 | 16 | 33
15" / 375mm Nominal Bore | - | - | - | - | - | -
16" / 400mm Nominal Bore | 420 | 515 | 620 | 550 | 16 | 36
18" / 450mm Nominal Bore | 470 | 565 | - | - | - | -
20" / 500mm Nominal Bore | 520 | 625 | 730 | 660 | 20 | 36
22" / 550mm Nominal Bore | - | - | - | - | - | -
24" / 600mm Nominal Bore | 620 | 730 | 845 | 770 | 20 | 39
26" / 650mm Nominal Bore | - | - | - | - | - | -
28" / 700mm Nominal Bore | 720 | 830 | 960 | 875 | 24 | 42
30" / 750mm Nominal Bore | - | - | - | - | - | -
32" / 800mm Nominal Bore | 820 | 940 | 1085 | 990 | 24 | 48
34" / 850mm Nominal Bore | - | - | - | - | - | -
36" / 900mm Nominal Bore | 920 | 1040 | 1185 | 1090 | 28 | 48
38" / 950mm Nominal Bore | - | - | - | - | - | -
40" / 1000mm Nominal Bore | 1020 | 1150 | 1320 | 1210 | 28 | 56
42" / 1050mm Nominal Bore | - | - | - | - | - | -
44" / 1100mm Nominal Bore | - | - | - | - | - | -
46" / 1150mm Nominal Bore | - | - | - | - | - | -
48" / 1200mm Nominal Bore | 1220 | 1360 | 1530 | 1420 | 30 | 56
50" / 1250mm Nominal Bore | - | - | - | - | - | -
52" / 1300mm Nominal Bore | - | - | - | - | - | -
54" / 1350mm Nominal Bore | - | - | - | - | - | -
56" / 1400mm Nominal Bore | 1420 | 1575 | 1755 | 1640 | 36 | 62
58" / 1450mm Nominal Bore | - | - | - | - | - | -
60" / 1500mm Nominal Bore | - | - | - | - | - | -